## Readme
Background information:
This calculator provides energy savings estimation for HVAC control retrofits to Guideline 36 sequences.
You can select choices from dropdown lists that make the scenario most closely represent your building and currently implemented control strategy.
The calculator will present the energy savings of Guideline 36 sequences against your current controls.
The results are based on simulation analysis of a particular building with a particular HVAC system. Buildings with different floor areas, central plant efficiencies, and utility costs are scaled using data from the simulation analysis. See the companion report for more details.
The building model is based on the DOE Commercial Reference Building Benchmarks with modified zoning to more closely represent a realistic office building. See the companion report for more details.

## Calculator (SI)
User guide
Input the scenario that most closely represents your building using the dropdown lists in the gray shaded cells in Tables 1 and 2.
Table 4 gives an overview of the available options in the drop down lists.
In Table 1, any numeric can be given for cooling and heating efficiencies, and electricity and gas utility rates.
In Table 2, you have the choice to select a primary or/and a secondary system. If there is no secondary system, set the secondary building size to 0.
Table 1: General |  |  | Legend: |  | Table 4: Input Data Overview
Climate | CA CZ6 (LA) |  | User inputs |  | Climate | Heating fuel | Building | Schedule (hr/week) | Internal loads | System Type | SAT Setpoint | DSP Setpoint | VAV Ctrl | Occ Control
Cooling efficiency (kW_thermal/kW_electric) | 3.2 |  |  |  | CA CZ3 (San Francisco) | Electric | Office | 50 | High | VAVR | Fixed | Fixed | Single Max (30%) | No
Heating fuel | Electric |  |  |  | CA CZ6 (LA) | Gas |  | 75 | Medium |  | OAT Reset | Limiting Reset | Single Max (20%)
Heating efficiency (kW_thermal/kW_gas or kW_elec) | 4 |  |  |  | CA CZ12 (Sacramento) |  |  | 105 | Low |  | T&R Reset | T&R Reset | Dual Max
Electricity utility rate ($/kWh) | 0.06
Gas utility rate ($/kWh) | 0.03
Table 2: Use/System Type
Attribute Type | Attribute | Primary | Secondary
Building Attributes | Size (m2) | 1662 | 0
| Building Type | Office | Office
Use Attributes | Schedule (hr/wk) | 105 | 105
| Load Magnitude | High | Low
(E) HVAC System Attributes | System Type | VAVR | VAVR
| SAT Setpoint | OAT Reset | Fixed
| DSP Setpoint | Limiting Reset | Fixed
| VAV Control | Single Max (30%) | Single Max (20%)
Retrofit HVAC System Attributes | Occupancy Control | No | No
Table 3: Predicted Energy Use and Savings
| Baseline | Guideline 36 | Savings | Savings %
Cooling (kWh/yr) | 21677.5661 | 18986.9402 | 2690.6259 | 12.412 | 13.0431
Heating (kWh/yr) | 215.347 | 27.4583 | 187.8886 | 87.2493 | 0.12957
Fan (kWh/yr) | 4142.5909 | 2577.1466 | 1565.4443 | 37.789 | 2.4925
HVAC (kWh/yr) | 26035.504 | 21591.5451 | 4443.9588 | 17.0688 | 15.6652
Lighting and Equipment (kWh/yr) | 120760.92 | 120760.92 | 0 | 0 | 72.66
Whole Building EUI (kWh/m2) | 88.3252 | 85.6513 | 2.6739 | 3.0273
Utility: Electricity (kWh/yr) | 146796.424 | 142352.4651 | 4443.9588 | 3.0273
Utility: Gas (kWh/yr) | 0 | 0 | 0 | 0
Energy Cost ($/yr) | 8807.7854 | 8541.1479 | 266.6375 | 3.0273

## Calculator (IP)
User guide
Input the scenario that most closely represents your building using the dropdown lists in the gray shaded cells in Tables 1 and 2.
Table 4 gives an overview of the available options in the drop down lists.
In Table 1, any numeric can be given for cooling and heating efficiencies, and electricity and gas utility rates.
In Table 2, you have the choice to select a primary or/and a secondary system. If there is no secondary system, set the secondary building size to 0.
Table 1: General |  |  | Legend: |  | Table 4: Input Data Overview
Climate | CA CZ12 (Sacramento) |  | User inputs |  | Climate | Heating fuel | Building | Schedule (hr/week) | Internal loads | System Type | SAT Setpoint | DSP Setpoint | VAV Ctrl | Occ Control
Cooling efficiency (kW/ton) | 1.099 |  |  |  | CA CZ3 (San Francisco) | Electric | Office | 50 | High | VAVR | Fixed | Fixed | Single Max (30%) | No
Heating fuel | Electric |  |  |  | CA CZ6 (LA) | Gas |  | 75 | Medium |  | OAT Reset | Limiting Reset | Single Max (20%)
Heating efficiency (kBtu_thermal/kBtu_gas or kBtu_elec) | 0.8 |  |  |  | CA CZ12 (Sacramento) |  |  | 105 | Low |  | T&R Reset | T&R Reset | Dual Max
Electricity utility rate ($/kWh) | 0.06
Gas utility rate ($/therm) | 0.03
Table 2: Use/System Type
Attribute Type | Attribute | Primary | Secondary
Building Attributes | Size (ft2) | 17889.62 | 17889.62
| Building Type | Office | Office
Use Attributes | Schedule (hr/wk) | 105 | 105
| Load Magnitude | Low | Low
(E) HVAC System Attributes | System Type | VAVR | VAVR
| SAT Setpoint | Fixed | Fixed
| DSP Setpoint | Limiting Reset | Fixed
| VAV Control | Single Max (30%) | Single Max (30%)
Retrofit HVAC System Attributes | Occupancy Control | No | No
Table 3: Predicted Energy Use and Savings
| Baseline | Guideline 36 | Savings | Savings %
Cooling (kBtu/yr) | 194090.9614 | 140083.8246 | 54007.1368 | 27.8257 | 5.4247
Heating (kBtu/yr) | 406214.9815 | 101455.0575 | 304759.924 | 75.0243 | 11.3534
Fan (kBtu/yr) | 45540.5757 | 11954.3302 | 33586.2455 | 73.7502 | 1.2728
HVAC (kBtu/yr) | 645846.5186 | 253493.2123 | 392353.3063 | 60.7502 | 18.0509
Lighting and Equipment (kBtu/yr) | 247232.1509 | 247232.1509 | 0 | 0 | 6.9099
Whole Building EUI (kBtu/ft2) | 24.9608 | 13.9949 | 10.9659 | 43.9327
Utility: Electricity (kWh/yr) | 261735.4587 | 146748.0829 | 114987.3758 | 43.9327
Utility: Gas (therms/yr) | 0 | 0 | 0 | 0
Energy Cost ($/yr) | 15704.1275 | 8804.885 | 6899.2426 | 43.9327

## data
Unit conversion | 1 | 3.4121 | 1 | 10.7639 | 1 | 0.317
| kWh | kBtu | m2 | ft2 | kWh/m2 | kBtu/ft2
[5 empty] | SI |  |  | IP |  |  |  |  | SI | IP
| Control | Climate | Load | Hours | Ecoo (kWh/m2) | Ehea (kWh/m2) | Efan (kWh/m2) | Ecoo (kBtu/ft2) | Ehea (kBtu/ft2) | Efan (kBtu/ft2) | Operation hours | Loads | Elig_equ(kWh/m2) | Elig_equ(kBtu/ft2)
A1B1C2_LA_hLoad_hHours | A1B1C2 | CA CZ6 (LA) | High | 105 | 56.1044 | 1.0822 | 4.1766 | 17.785 | 0.34305 | 1.324 | 105 | High | 72.66 | 23.0331
A1B1C2_LA_hLoad_lHours | A1B1C2 | CA CZ6 (LA) | High | 50 | 37.9401 | 0.13631 | 2.6647 | 12.027 | 0.043211 | 0.84471 | 75 | High | 57.86 | 18.3415
A1B1C2_LA_hLoad_mHours | A1B1C2 | CA CZ6 (LA) | High | 75 | 45.5603 | 0.47354 | 3.2873 | 14.4425 | 0.15011 | 1.0421 | 50 | High | 46.61 | 14.7753
A1B1C2_LA_lLoad_hHours | A1B1C2 | CA CZ6 (LA) | Low | 105 | 50.805 | 7.0735 | 3.9122 | 16.1051 | 2.2423 | 1.2401 | 105 | Medium | 43.596 | 13.8199
A1B1C2_LA_lLoad_lHours | A1B1C2 | CA CZ6 (LA) | Low | 50 | 31.6511 | 0.99713 | 2.2001 | 10.0333 | 0.31609 | 0.69743 | 75 | Medium | 34.716 | 11.0049
A1B1C2_LA_lLoad_mHours | A1B1C2 | CA CZ6 (LA) | Low | 75 | 39.9446 | 3.1787 | 2.9478 | 12.6624 | 1.0076 | 0.93446 | 50 | Medium | 27.966 | 8.8652
A1B1C2_LA_mLoad_hHours | A1B1C2 | CA CZ6 (LA) | Medium | 105 | 52.6908 | 3.4378 | 3.9919 | 16.7029 | 1.0898 | 1.2654 | 105 | Low | 21.798 | 6.9099
A1B1C2_LA_mLoad_lHours | A1B1C2 | CA CZ6 (LA) | Medium | 50 | 33.8625 | 0.40019 | 2.3505 | 10.7344 | 0.12686 | 0.7451 | 75 | Low | 17.358 | 5.5025
A1B1C2_LA_mLoad_mHours | A1B1C2 | CA CZ6 (LA) | Medium | 75 | 42.0147 | 1.3973 | 3.0584 | 13.3186 | 0.44295 | 0.9695 | 50 | Low | 13.983 | 4.4326
A1B1C2_SAC_hLoad_hHours | A1B1C2 | CA CZ12 (Sacramento) | High | 105 | 53.4638 | 8.4562 | 4.7167 | 16.9479 | 2.6806 | 1.4952
A1B1C2_SAC_hLoad_lHours | A1B1C2 | CA CZ12 (Sacramento) | High | 50 | 38.4177 | 3.7938 | 3.1888 | 12.1784 | 1.2026 | 1.0108
A1B1C2_SAC_hLoad_mHours | A1B1C2 | CA CZ12 (Sacramento) | High | 75 | 45.4439 | 6.0638 | 3.8132 | 14.4056 | 1.9222 | 1.2088
A1B1C2_SAC_lLoad_hHours | A1B1C2 | CA CZ12 (Sacramento) | Low | 105 | 47.6135 | 16.3663 | 4.3535 | 15.0934 | 5.1881 | 1.3801
A1B1C2_SAC_lLoad_lHours | A1B1C2 | CA CZ12 (Sacramento) | Low | 50 | 32.8803 | 7.0005 | 2.6691 | 10.423 | 2.2191 | 0.8461
A1B1C2_SAC_lLoad_mHours | A1B1C2 | CA CZ12 (Sacramento) | Low | 75 | 39.7496 | 11.0492 | 3.4065 | 12.6006 | 3.5026 | 1.0799
A1B1C2_SAC_mLoad_hHours | A1B1C2 | CA CZ12 (Sacramento) | Medium | 105 | 49.7424 | 12.2225 | 4.4842 | 15.7683 | 3.8745 | 1.4215
A1B1C2_SAC_mLoad_lHours | A1B1C2 | CA CZ12 (Sacramento) | Medium | 50 | 35.0295 | 5.4072 | 2.8551 | 11.1043 | 1.7141 | 0.90507
A1B1C2_SAC_mLoad_mHours | A1B1C2 | CA CZ12 (Sacramento) | Medium | 75 | 41.9799 | 8.5179 | 3.5551 | 13.3076 | 2.7002 | 1.1269
A1B1C2_SF_hLoad_hHours | A1B1C2 | CA CZ3 (San Francisco) | High | 105 | 32.041 | 6.9755 | 4.8697 | 10.157 | 2.2112 | 1.5437
A1B1C2_SF_hLoad_lHours | A1B1C2 | CA CZ3 (San Francisco) | High | 50 | 21.5479 | 2.289 | 2.8277 | 6.8307 | 0.7256 | 0.89638
A1B1C2_SF_hLoad_mHours | A1B1C2 | CA CZ3 (San Francisco) | High | 75 | 26.5008 | 4.3356 | 3.7217 | 8.4007 | 1.3744 | 1.1798
A1B1C2_SF_lLoad_hHours | A1B1C2 | CA CZ3 (San Francisco) | Low | 105 | 30.0762 | 15.5828 | 4.6796 | 9.5341 | 4.9397 | 1.4834
A1B1C2_SF_lLoad_lHours | A1B1C2 | CA CZ3 (San Francisco) | Low | 50 | 19.1106 | 4.7353 | 2.5306 | 6.058 | 1.5011 | 0.8022
A1B1C2_SF_lLoad_mHours | A1B1C2 | CA CZ3 (San Francisco) | Low | 75 | 24.4417 | 9.1687 | 3.5001 | 7.748 | 2.9064 | 1.1095
A1B1C2_SF_mLoad_hHours | A1B1C2 | CA CZ3 (San Francisco) | Medium | 105 | 30.7723 | 10.9619 | 4.7454 | 9.7548 | 3.4749 | 1.5043
A1B1C2_SF_mLoad_lHours | A1B1C2 | CA CZ3 (San Francisco) | Medium | 50 | 19.9222 | 3.4108 | 2.625 | 6.3153 | 1.0812 | 0.83211
A1B1C2_SF_mLoad_mHours | A1B1C2 | CA CZ3 (San Francisco) | Medium | 75 | 25.1851 | 6.4558 | 3.5764 | 7.9836 | 2.0465 | 1.1337
A1B2C1_LA_hLoad_hHours | A1B2C1 | CA CZ6 (LA) | High | 105 | 46.614 | 0.49196 | 6.2839 | 14.7766 | 0.15595 | 1.992
A1B2C1_LA_hLoad_lHours | A1B2C1 | CA CZ6 (LA) | High | 50 | 32.7434 | 0.061675 | 3.6104 | 10.3796 | 0.019551 | 1.1445
A1B2C1_LA_hLoad_mHours | A1B2C1 | CA CZ6 (LA) | High | 75 | 38.9049 | 0.18035 | 4.765 | 12.3328 | 0.057172 | 1.5105
A1B2C1_LA_lLoad_hHours | A1B2C1 | CA CZ6 (LA) | Low | 105 | 42.5315 | 4.9914 | 6.0485 | 13.4824 | 1.5823 | 1.9174
A1B2C1_LA_lLoad_lHours | A1B2C1 | CA CZ6 (LA) | Low | 50 | 28.7201 | 0.46373 | 3.1935 | 9.1042 | 0.147 | 1.0123
A1B2C1_LA_lLoad_mHours | A1B2C1 | CA CZ6 (LA) | Low | 75 | 34.7874 | 2.1425 | 4.4746 | 11.0275 | 0.67918 | 1.4185
A1B2C1_LA_mLoad_hHours | A1B2C1 | CA CZ6 (LA) | Medium | 105 | 43.8895 | 2.0015 | 6.13 | 13.9129 | 0.63448 | 1.9432
A1B2C1_LA_mLoad_lHours | A1B2C1 | CA CZ6 (LA) | Medium | 50 | 30.3467 | 0.16394 | 3.3297 | 9.6199 | 0.051967 | 1.0555
A1B2C1_LA_mLoad_mHours | A1B2C1 | CA CZ6 (LA) | Medium | 75 | 36.4227 | 0.62161 | 4.5704 | 11.546 | 0.19705 | 1.4488
A1B2C1_SAC_hLoad_hHours | A1B2C1 | CA CZ12 (Sacramento) | High | 105 | 51.8127 | 4.1143 | 6.6454 | 16.4245 | 1.3042 | 2.1066
A1B2C1_SAC_hLoad_lHours | A1B2C1 | CA CZ12 (Sacramento) | High | 50 | 36.575 | 2.1288 | 3.9834 | 11.5942 | 0.67483 | 1.2627
A1B2C1_SAC_hLoad_mHours | A1B2C1 | CA CZ12 (Sacramento) | High | 75 | 43.7747 | 3.1278 | 5.1291 | 13.8765 | 0.99151 | 1.6259
A1B2C1_SAC_lLoad_hHours | A1B2C1 | CA CZ12 (Sacramento) | Low | 105 | 48.1842 | 11.9214 | 6.3802 | 15.2743 | 3.7791 | 2.0225
A1B2C1_SAC_lLoad_lHours | A1B2C1 | CA CZ12 (Sacramento) | Low | 50 | 32.1553 | 4.6347 | 3.5474 | 10.1932 | 1.4692 | 1.1245
A1B2C1_SAC_lLoad_mHours | A1B2C1 | CA CZ12 (Sacramento) | Low | 75 | 39.6406 | 7.8105 | 4.7944 | 12.566 | 2.4759 | 1.5198
A1B2C1_SAC_mLoad_hHours | A1B2C1 | CA CZ12 (Sacramento) | Medium | 105 | 49.3621 | 7.6515 | 6.4697 | 15.6477 | 2.4255 | 2.0509
A1B2C1_SAC_mLoad_lHours | A1B2C1 | CA CZ12 (Sacramento) | Medium | 50 | 33.912 | 3.2754 | 3.7039 | 10.75 | 1.0383 | 1.1741
A1B2C1_SAC_mLoad_mHours | A1B2C1 | CA CZ12 (Sacramento) | Medium | 75 | 41.1193 | 5.0924 | 4.9124 | 13.0347 | 1.6143 | 1.5572
A1B2C1_SF_hLoad_hHours | A1B2C1 | CA CZ3 (San Francisco) | High | 105 | 19.3105 | 2.6309 | 7.7949 | 6.1214 | 0.83399 | 2.471
A1B2C1_SF_hLoad_lHours | A1B2C1 | CA CZ3 (San Francisco) | High | 50 | 13.8646 | 1.0028 | 4.4804 | 4.395 | 0.31788 | 1.4203
A1B2C1_SF_hLoad_mHours | A1B2C1 | CA CZ3 (San Francisco) | High | 75 | 16.6947 | 1.8082 | 5.9395 | 5.2922 | 0.57318 | 1.8828
A1B2C1_SF_lLoad_hHours | A1B2C1 | CA CZ3 (San Francisco) | Low | 105 | 18.1536 | 7.6094 | 7.5058 | 5.7547 | 2.4122 | 2.3793
A1B2C1_SF_lLoad_lHours | A1B2C1 | CA CZ3 (San Francisco) | Low | 50 | 12.5885 | 2.378 | 4.0507 | 3.9905 | 0.75382 | 1.2841
A1B2C1_SF_lLoad_mHours | A1B2C1 | CA CZ3 (San Francisco) | Low | 75 | 15.5346 | 4.4667 | 5.6179 | 4.9244 | 1.4159 | 1.7809
A1B2C1_SF_mLoad_hHours | A1B2C1 | CA CZ3 (San Francisco) | Medium | 105 | 18.5763 | 4.6058 | 7.6165 | 5.8886 | 1.46 | 2.4144
A1B2C1_SF_mLoad_lHours | A1B2C1 | CA CZ3 (San Francisco) | Medium | 50 | 13.0627 | 1.6526 | 4.1932 | 4.1409 | 0.52386 | 1.3292
A1B2C1_SF_mLoad_mHours | A1B2C1 | CA CZ3 (San Francisco) | Medium | 75 | 15.972 | 2.8886 | 5.7341 | 5.0631 | 0.91568 | 1.8177
A1B2C2_LA_hLoad_hHours | A1B2C2 | CA CZ6 (LA) | High | 105 | 40.0796 | 0.094052 | 4.7493 | 12.7052 | 0.029814 | 1.5055
A1B2C2_LA_hLoad_lHours | A1B2C2 | CA CZ6 (LA) | High | 50 | 30.9355 | 0.02467 | 3.2338 | 9.8065 | 0.0078202 | 1.0251
A1B2C2_LA_hLoad_mHours | A1B2C2 | CA CZ6 (LA) | High | 75 | 34.7889 | 0.063288 | 3.8678 | 11.028 | 0.020062 | 1.2261
A1B2C2_LA_lLoad_hHours | A1B2C2 | CA CZ6 (LA) | Low | 105 | 34.3407 | 0.97269 | 4.155 | 10.8859 | 0.30834 | 1.3171
A1B2C2_LA_lLoad_lHours | A1B2C2 | CA CZ6 (LA) | Low | 50 | 24.8746 | 0.15372 | 2.4578 | 7.8852 | 0.048728 | 0.77913
A1B2C2_LA_lLoad_mHours | A1B2C2 | CA CZ6 (LA) | Low | 75 | 29.0411 | 0.38515 | 3.208 | 9.206 | 0.12209 | 1.0169
A1B2C2_LA_mLoad_hHours | A1B2C2 | CA CZ6 (LA) | Medium | 105 | 36.4643 | 0.24674 | 4.3289 | 11.5591 | 0.078217 | 1.3723
A1B2C2_LA_mLoad_lHours | A1B2C2 | CA CZ6 (LA) | Medium | 50 | 27.0228 | 0.06629 | 2.692 | 8.5662 | 0.021014 | 0.85335
A1B2C2_LA_mLoad_mHours | A1B2C2 | CA CZ6 (LA) | Medium | 75 | 31.1943 | 0.1494 | 3.4128 | 9.8886 | 0.047361 | 1.0819
A1B2C2_SAC_hLoad_hHours | A1B2C2 | CA CZ12 (Sacramento) | High | 105 | 47.4814 | 3.1406 | 5.0045 | 15.0515 | 0.99557 | 1.5864
A1B2C2_SAC_hLoad_lHours | A1B2C2 | CA CZ12 (Sacramento) | High | 50 | 35.5046 | 1.8254 | 3.4672 | 11.2549 | 0.57864 | 1.0991
A1B2C2_SAC_hLoad_mHours | A1B2C2 | CA CZ12 (Sacramento) | High | 75 | 41.2734 | 2.6377 | 4.1064 | 13.0836 | 0.83615 | 1.3017
A1B2C2_SAC_lLoad_hHours | A1B2C2 | CA CZ12 (Sacramento) | Low | 105 | 41.436 | 7.7155 | 4.5092 | 13.1352 | 2.4458 | 1.4294
A1B2C2_SAC_lLoad_lHours | A1B2C2 | CA CZ12 (Sacramento) | Low | 50 | 30.0461 | 3.9075 | 2.8186 | 9.5246 | 1.2387 | 0.89348
A1B2C2_SAC_lLoad_mHours | A1B2C2 | CA CZ12 (Sacramento) | Low | 75 | 35.6203 | 5.6754 | 3.5651 | 11.2916 | 1.7991 | 1.1301
A1B2C2_SAC_mLoad_hHours | A1B2C2 | CA CZ12 (Sacramento) | Medium | 105 | 43.7202 | 5.0786 | 4.6853 | 13.8593 | 1.6099 | 1.4852
A1B2C2_SAC_mLoad_lHours | A1B2C2 | CA CZ12 (Sacramento) | Medium | 50 | 32.1942 | 2.8321 | 3.0464 | 10.2055 | 0.89777 | 0.96571
A1B2C2_SAC_mLoad_mHours | A1B2C2 | CA CZ12 (Sacramento) | Medium | 75 | 37.8788 | 4.1062 | 3.7554 | 12.0075 | 1.3016 | 1.1904
A1B2C2_SF_hLoad_hHours | A1B2C2 | CA CZ3 (San Francisco) | High | 105 | 16.7217 | 1.512 | 5.7993 | 5.3008 | 0.47932 | 1.8384
A1B2C2_SF_hLoad_lHours | A1B2C2 | CA CZ3 (San Francisco) | High | 50 | 12.9347 | 0.67432 | 3.8374 | 4.1003 | 0.21376 | 1.2164
A1B2C2_SF_hLoad_mHours | A1B2C2 | CA CZ3 (San Francisco) | High | 75 | 14.8759 | 1.1544 | 4.7058 | 4.7156 | 0.36596 | 1.4917
A1B2C2_SF_lLoad_hHours | A1B2C2 | CA CZ3 (San Francisco) | Low | 105 | 14.7714 | 4.1107 | 5.2374 | 4.6825 | 1.3031 | 1.6603
A1B2C2_SF_lLoad_lHours | A1B2C2 | CA CZ3 (San Francisco) | Low | 50 | 10.8171 | 1.7386 | 3.0843 | 3.429 | 0.55112 | 0.97773
A1B2C2_SF_lLoad_mHours | A1B2C2 | CA CZ3 (San Francisco) | Low | 75 | 12.9235 | 2.8839 | 4.065 | 4.0967 | 0.9142 | 1.2886
A1B2C2_SF_mLoad_hHours | A1B2C2 | CA CZ3 (San Francisco) | Medium | 105 | 15.5026 | 2.6665 | 5.409 | 4.9143 | 0.84528 | 1.7146
A1B2C2_SF_mLoad_lHours | A1B2C2 | CA CZ3 (San Francisco) | Medium | 50 | 11.547 | 1.17 | 3.3123 | 3.6604 | 0.37088 | 1.05
A1B2C2_SF_mLoad_mHours | A1B2C2 | CA CZ3 (San Francisco) | Medium | 75 | 13.6261 | 1.9707 | 4.2519 | 4.3194 | 0.62471 | 1.3479
A2B1C1_LA_hLoad_hHours | A2B1C1 | CA CZ6 (LA) | High | 105 | 61.8151 | 6.0742 | 1.8189 | 19.5953 | 1.9255 | 0.57659
A2B1C1_LA_hLoad_lHours | A2B1C1 | CA CZ6 (LA) | High | 50 | 39.0431 | 0.64074 | 1.6031 | 12.3766 | 0.20311 | 0.50819
A2B1C1_LA_hLoad_mHours | A2B1C1 | CA CZ6 (LA) | High | 75 | 48.8751 | 2.371 | 1.6128 | 15.4933 | 0.7516 | 0.51127
A2B1C1_LA_lLoad_hHours | A2B1C1 | CA CZ6 (LA) | Low | 105 | 58.0987 | 17.2066 | 1.5901 | 18.4172 | 5.4545 | 0.50405
A2B1C1_LA_lLoad_lHours | A2B1C1 | CA CZ6 (LA) | Low | 50 | 34.6765 | 3.2746 | 1.1766 | 10.9924 | 1.038 | 0.37297
A2B1C1_LA_lLoad_mHours | A2B1C1 | CA CZ6 (LA) | Low | 75 | 44.8086 | 9.054 | 1.3198 | 14.2043 | 2.8701 | 0.41838
A2B1C1_LA_mLoad_hHours | A2B1C1 | CA CZ6 (LA) | Medium | 105 | 59.355 | 11.6263 | 1.6687 | 18.8154 | 3.6855 | 0.52896
A2B1C1_LA_mLoad_lHours | A2B1C1 | CA CZ6 (LA) | Medium | 50 | 36.3808 | 1.624 | 1.3244 | 11.5327 | 0.5148 | 0.41983
A2B1C1_LA_mLoad_mHours | A2B1C1 | CA CZ6 (LA) | Medium | 75 | 46.2444 | 5.3682 | 1.4195 | 14.6594 | 1.7017 | 0.44997
A2B1C1_SAC_hLoad_hHours | A2B1C1 | CA CZ12 (Sacramento) | High | 105 | 55.6322 | 16.4858 | 2.0908 | 17.6353 | 5.226 | 0.66278
A2B1C1_SAC_hLoad_lHours | A2B1C1 | CA CZ12 (Sacramento) | High | 50 | 38.8023 | 6.3357 | 2.1492 | 12.3003 | 2.0084 | 0.6813
A2B1C1_SAC_hLoad_mHours | A2B1C1 | CA CZ12 (Sacramento) | High | 75 | 46.4547 | 10.7171 | 2.034 | 14.7261 | 3.3973 | 0.64478
A2B1C1_SAC_lLoad_hHours | A2B1C1 | CA CZ12 (Sacramento) | Low | 105 | 51.9125 | 28.1469 | 1.7621 | 16.4562 | 8.9225 | 0.55857
A2B1C1_SAC_lLoad_lHours | A2B1C1 | CA CZ12 (Sacramento) | Low | 50 | 34.1751 | 10.5864 | 1.6134 | 10.8335 | 3.3559 | 0.51145
A2B1C1_SAC_lLoad_mHours | A2B1C1 | CA CZ12 (Sacramento) | Low | 75 | 42.1469 | 18.2004 | 1.6137 | 13.3605 | 5.7695 | 0.51153
A2B1C1_SAC_mLoad_hHours | A2B1C1 | CA CZ12 (Sacramento) | Medium | 105 | 53.1475 | 22.5471 | 1.8769 | 16.8477 | 7.1474 | 0.59497
A2B1C1_SAC_mLoad_lHours | A2B1C1 | CA CZ12 (Sacramento) | Medium | 50 | 35.9908 | 8.5136 | 1.8143 | 11.409 | 2.6988 | 0.57512
A2B1C1_SAC_mLoad_mHours | A2B1C1 | CA CZ12 (Sacramento) | Medium | 75 | 43.6855 | 14.4867 | 1.765 | 13.8482 | 4.5923 | 0.5595
A2B1C1_SF_hLoad_hHours | A2B1C1 | CA CZ3 (San Francisco) | High | 105 | 34.8292 | 16.3297 | 2.2123 | 11.0408 | 5.1765 | 0.70129
A2B1C1_SF_hLoad_lHours | A2B1C1 | CA CZ3 (San Francisco) | High | 50 | 22.4948 | 4.3983 | 1.6279 | 7.1308 | 1.3942 | 0.51605
A2B1C1_SF_hLoad_mHours | A2B1C1 | CA CZ3 (San Francisco) | High | 75 | 28.4514 | 9.0285 | 1.8495 | 9.0191 | 2.862 | 0.5863
A2B1C1_SF_lLoad_hHours | A2B1C1 | CA CZ3 (San Francisco) | Low | 105 | 33.5689 | 29.3579 | 2.0249 | 10.6413 | 9.3064 | 0.64188
A2B1C1_SF_lLoad_lHours | A2B1C1 | CA CZ3 (San Francisco) | Low | 50 | 20.9778 | 8.7077 | 1.3538 | 6.6499 | 2.7603 | 0.42914
A2B1C1_SF_lLoad_mHours | A2B1C1 | CA CZ3 (San Francisco) | Low | 75 | 27.1234 | 17.5178 | 1.6333 | 8.5981 | 5.5531 | 0.51776
A2B1C1_SF_mLoad_hHours | A2B1C1 | CA CZ3 (San Francisco) | Medium | 105 | 34.0247 | 23.2039 | 2.0936 | 10.7858 | 7.3556 | 0.66368
A2B1C1_SF_mLoad_lHours | A2B1C1 | CA CZ3 (San Francisco) | Medium | 50 | 21.5422 | 6.3578 | 1.4537 | 6.8288 | 2.0154 | 0.46083
A2B1C1_SF_mLoad_mHours | A2B1C1 | CA CZ3 (San Francisco) | Medium | 75 | 27.6018 | 13.2506 | 1.7118 | 8.7497 | 4.2004 | 0.54264
A2B1C2_LA_hLoad_hHours | A2B1C2 | CA CZ6 (LA) | High | 105 | 49.7159 | 0.80396 | 1.2701 | 15.7599 | 0.25485 | 0.40261 |  |  |  |  | #DIV/0!
A2B1C2_LA_hLoad_lHours | A2B1C2 | CA CZ6 (LA) | High | 50 | 35.5216 | 0.11594 | 1.42 | 11.2603 | 0.036751 | 0.45013
A2B1C2_LA_hLoad_mHours | A2B1C2 | CA CZ6 (LA) | High | 75 | 41.4489 | 0.38167 | 1.2645 | 13.1392 | 0.12099 | 0.40085
A2B1C2_LA_lLoad_hHours | A2B1C2 | CA CZ6 (LA) | Low | 105 | 43.9179 | 5.8303 | 0.9243 | 13.9219 | 1.8482 | 0.293
A2B1C2_LA_lLoad_lHours | A2B1C2 | CA CZ6 (LA) | Low | 50 | 28.7739 | 0.82438 | 0.87737 | 9.1213 | 0.26133 | 0.27812
A2B1C2_LA_lLoad_mHours | A2B1C2 | CA CZ6 (LA) | Low | 75 | 35.2305 | 2.6027 | 0.8523 | 11.168 | 0.82505 | 0.27018
A2B1C2_LA_mLoad_hHours | A2B1C2 | CA CZ6 (LA) | Medium | 105 | 45.9337 | 2.6377 | 1.0372 | 14.5609 | 0.83615 | 0.3288
A2B1C2_LA_mLoad_lHours | A2B1C2 | CA CZ6 (LA) | Medium | 50 | 31.1991 | 0.33286 | 1.0684 | 9.8901 | 0.10551 | 0.33868
A2B1C2_LA_mLoad_mHours | A2B1C2 | CA CZ6 (LA) | Medium | 75 | 37.4984 | 1.1174 | 0.9946 | 11.8869 | 0.3542 | 0.31529
A2B1C2_SAC_hLoad_hHours | A2B1C2 | CA CZ12 (Sacramento) | High | 105 | 49.6763 | 8.044 | 1.5916 | 15.7473 | 2.5499 | 0.50454
A2B1C2_SAC_hLoad_lHours | A2B1C2 | CA CZ12 (Sacramento) | High | 50 | 37.1288 | 3.6553 | 1.9622 | 11.7698 | 1.1587 | 0.622
A2B1C2_SAC_hLoad_mHours | A2B1C2 | CA CZ12 (Sacramento) | High | 75 | 43.0827 | 5.8204 | 1.6981 | 13.6572 | 1.8451 | 0.53831
A2B1C2_SAC_lLoad_hHours | A2B1C2 | CA CZ12 (Sacramento) | Low | 105 | 43.3757 | 15.4228 | 1.1512 | 13.75 | 4.889 | 0.36493
A2B1C2_SAC_lLoad_lHours | A2B1C2 | CA CZ12 (Sacramento) | Low | 50 | 31.3156 | 6.7534 | 1.3322 | 9.927 | 2.1408 | 0.42231
A2B1C2_SAC_lLoad_mHours | A2B1C2 | CA CZ12 (Sacramento) | Low | 75 | 37.0192 | 10.5661 | 1.1824 | 11.735 | 3.3494 | 0.37483
A2B1C2_SAC_mLoad_hHours | A2B1C2 | CA CZ12 (Sacramento) | Medium | 105 | 45.7122 | 11.5379 | 1.3088 | 14.4907 | 3.6575 | 0.41488
A2B1C2_SAC_mLoad_lHours | A2B1C2 | CA CZ12 (Sacramento) | Medium | 50 | 33.5888 | 5.21 | 1.5684 | 10.6476 | 1.6516 | 0.49717
A2B1C2_SAC_mLoad_mHours | A2B1C2 | CA CZ12 (Sacramento) | Medium | 75 | 39.3949 | 8.175 | 1.3732 | 12.4881 | 2.5915 | 0.4353
A2B1C2_SF_hLoad_hHours | A2B1C2 | CA CZ3 (San Francisco) | High | 105 | 27.2422 | 6.3802 | 1.3979 | 8.6357 | 2.0225 | 0.44312
A2B1C2_SF_hLoad_lHours | A2B1C2 | CA CZ3 (San Francisco) | High | 50 | 19.479 | 2.1569 | 1.2814 | 6.1748 | 0.68374 | 0.40621
A2B1C2_SF_hLoad_mHours | A2B1C2 | CA CZ3 (San Francisco) | High | 75 | 23.1465 | 4.0376 | 1.2875 | 7.3374 | 1.2799 | 0.40814
A2B1C2_SF_lLoad_hHours | A2B1C2 | CA CZ3 (San Francisco) | Low | 105 | 24.9694 | 14.1704 | 1.1437 | 7.9153 | 4.492 | 0.36255
A2B1C2_SF_lLoad_lHours | A2B1C2 | CA CZ3 (San Francisco) | Low | 50 | 16.7719 | 4.4523 | 0.92359 | 5.3167 | 1.4114 | 0.29278
A2B1C2_SF_lLoad_mHours | A2B1C2 | CA CZ3 (San Francisco) | Low | 75 | 20.7727 | 8.4086 | 0.99922 | 6.5849 | 2.6655 | 0.31675
A2B1C2_SF_mLoad_hHours | A2B1C2 | CA CZ3 (San Francisco) | Medium | 105 | 25.76 | 9.9007 | 1.232 | 8.1659 | 3.1385 | 0.39055
A2B1C2_SF_mLoad_lHours | A2B1C2 | CA CZ3 (San Francisco) | Medium | 50 | 17.679 | 3.2162 | 1.0465 | 5.6042 | 1.0195 | 0.33173
A2B1C2_SF_mLoad_mHours | A2B1C2 | CA CZ3 (San Francisco) | Medium | 75 | 21.6309 | 5.9868 | 1.1009 | 6.857 | 1.8978 | 0.349
A2B2C1_LA_hLoad_hHours | A2B2C1 | CA CZ6 (LA) | High | 105 | 41.7378 | 0.51828 | 2.4925 | 13.2308 | 0.1643 | 0.79013
A2B2C1_LA_hLoad_lHours | A2B2C1 | CA CZ6 (LA) | High | 50 | 30.835 | 0.074494 | 2.2952 | 9.7746 | 0.023614 | 0.72757
A2B2C1_LA_hLoad_mHours | A2B2C1 | CA CZ6 (LA) | High | 75 | 35.5823 | 0.22372 | 2.3325 | 11.2795 | 0.07092 | 0.73939
A2B2C1_LA_lLoad_hHours | A2B2C1 | CA CZ6 (LA) | Low | 105 | 37.3527 | 4.9803 | 1.9546 | 11.8407 | 1.5787 | 0.61961
A2B2C1_LA_lLoad_lHours | A2B2C1 | CA CZ6 (LA) | Low | 50 | 26.3654 | 0.48853 | 1.5827 | 8.3578 | 0.15486 | 0.50171
A2B2C1_LA_lLoad_mHours | A2B2C1 | CA CZ6 (LA) | Low | 75 | 31.081 | 2.1012 | 1.7202 | 9.8526 | 0.66607 | 0.54529
A2B2C1_LA_mLoad_hHours | A2B2C1 | CA CZ6 (LA) | Medium | 105 | 38.8218 | 2.009 | 2.145 | 12.3064 | 0.63683 | 0.67997
A2B2C1_LA_mLoad_lHours | A2B2C1 | CA CZ6 (LA) | Medium | 50 | 28.1278 | 0.18949 | 1.8459 | 8.9165 | 0.060069 | 0.58516
A2B2C1_LA_mLoad_mHours | A2B2C1 | CA CZ6 (LA) | Medium | 75 | 32.8476 | 0.63036 | 1.9377 | 10.4126 | 0.19982 | 0.61425
A2B2C1_SAC_hLoad_hHours | A2B2C1 | CA CZ12 (Sacramento) | High | 105 | 48.6183 | 4.7426 | 2.5424 | 15.4119 | 1.5034 | 0.80592
A2B2C1_SAC_hLoad_lHours | A2B2C1 | CA CZ12 (Sacramento) | High | 50 | 35.6958 | 2.398 | 2.5771 | 11.3155 | 0.76015 | 0.81693
A2B2C1_SAC_hLoad_mHours | A2B2C1 | CA CZ12 (Sacramento) | High | 75 | 41.8981 | 3.6019 | 2.5015 | 13.2816 | 1.1418 | 0.79296
A2B2C1_SAC_lLoad_hHours | A2B2C1 | CA CZ12 (Sacramento) | Low | 105 | 44.458 | 12.6819 | 2.0002 | 14.0931 | 4.0201 | 0.63405
A2B2C1_SAC_lLoad_lHours | A2B2C1 | CA CZ12 (Sacramento) | Low | 50 | 30.9375 | 5.0488 | 1.8829 | 9.8071 | 1.6005 | 0.59688
A2B2C1_SAC_lLoad_mHours | A2B2C1 | CA CZ12 (Sacramento) | Low | 75 | 37.2955 | 8.3865 | 1.8876 | 11.8226 | 2.6585 | 0.59836
A2B2C1_SAC_mLoad_hHours | A2B2C1 | CA CZ12 (Sacramento) | Medium | 105 | 45.8603 | 8.4191 | 2.1903 | 14.5376 | 2.6688 | 0.69431
A2B2C1_SAC_mLoad_lHours | A2B2C1 | CA CZ12 (Sacramento) | Medium | 50 | 32.8388 | 3.6322 | 2.1436 | 10.4099 | 1.1514 | 0.67952
A2B2C1_SAC_mLoad_mHours | A2B2C1 | CA CZ12 (Sacramento) | Medium | 75 | 38.9752 | 5.6572 | 2.1109 | 12.3551 | 1.7933 | 0.66916
A2B2C1_SF_hLoad_hHours | A2B2C1 | CA CZ3 (San Francisco) | High | 105 | 17.4312 | 3.1402 | 3.4085 | 5.5257 | 0.99543 | 1.0805
A2B2C1_SF_hLoad_lHours | A2B2C1 | CA CZ3 (San Francisco) | High | 50 | 13.047 | 1.1432 | 2.8671 | 4.1359 | 0.3624 | 0.90888
A2B2C1_SF_hLoad_mHours | A2B2C1 | CA CZ3 (San Francisco) | High | 75 | 15.3261 | 2.1062 | 3.0774 | 4.8583 | 0.66767 | 0.97552
A2B2C1_SF_lLoad_hHours | A2B2C1 | CA CZ3 (San Francisco) | Low | 105 | 16.0601 | 8.6438 | 2.8469 | 5.091 | 2.7401 | 0.90246
A2B2C1_SF_lLoad_lHours | A2B2C1 | CA CZ3 (San Francisco) | Low | 50 | 11.5572 | 2.6348 | 2.2134 | 3.6636 | 0.83524 | 0.70163
A2B2C1_SF_lLoad_mHours | A2B2C1 | CA CZ3 (San Francisco) | Low | 75 | 13.9349 | 5.0135 | 2.4945 | 4.4173 | 1.5893 | 0.79074
A2B2C1_SF_mLoad_hHours | A2B2C1 | CA CZ3 (San Francisco) | Medium | 105 | 16.5613 | 5.3733 | 3.0579 | 5.2499 | 1.7033 | 0.96936
A2B2C1_SF_mLoad_lHours | A2B2C1 | CA CZ3 (San Francisco) | Medium | 50 | 12.1152 | 1.8501 | 2.449 | 3.8405 | 0.58647 | 0.77633
A2B2C1_SF_mLoad_mHours | A2B2C1 | CA CZ3 (San Francisco) | Medium | 75 | 14.4589 | 3.3045 | 2.7091 | 4.5835 | 1.0475 | 0.85878
BICBase_LA_hLoad_hHours | BICBase | CA CZ6 (LA) | High | 105 | 70.4728 | 7.1509 | 5.977 | 22.3398 | 2.2668 | 1.8947
BICBase_LA_hLoad_lHours | BICBase | CA CZ6 (LA) | High | 50 | 42.4189 | 0.73941 | 3.2269 | 13.4467 | 0.23439 | 1.0229
BICBase_LA_hLoad_mHours | BICBase | CA CZ6 (LA) | High | 75 | 54.7306 | 2.7878 | 4.4187 | 17.3495 | 0.88374 | 1.4007
BICBase_LA_lLoad_hHours | BICBase | CA CZ6 (LA) | Low | 105 | 66.9565 | 18.9273 | 5.8779 | 21.2251 | 5.9999 | 1.8633
BICBase_LA_lLoad_lHours | BICBase | CA CZ6 (LA) | Low | 50 | 38.4749 | 3.6996 | 3.0001 | 12.1965 | 1.1728 | 0.95103
BICBase_LA_lLoad_mHours | BICBase | CA CZ6 (LA) | Low | 75 | 50.9588 | 10.0547 | 4.2859 | 16.1539 | 3.1873 | 1.3586
BICBase_LA_mLoad_hHours | BICBase | CA CZ6 (LA) | Medium | 105 | 68.1344 | 13.1876 | 5.9126 | 21.5985 | 4.1804 | 1.8743
BICBase_LA_mLoad_lHours | BICBase | CA CZ6 (LA) | Medium | 50 | 40.0972 | 1.8673 | 3.0735 | 12.7107 | 0.59192 | 0.97428
BICBase_LA_mLoad_mHours | BICBase | CA CZ6 (LA) | Medium | 75 | 52.239 | 6.157 | 4.3306 | 16.5597 | 1.9517 | 1.3728
BICBase_SAC_hLoad_hHours | BICBase | CA CZ12 (Sacramento) | High | 105 | 60.8761 | 17.0616 | 6.4408 | 19.2976 | 5.4085 | 2.0417
BICBase_SAC_hLoad_lHours | BICBase | CA CZ12 (Sacramento) | High | 50 | 40.5151 | 6.4352 | 3.7611 | 12.8432 | 2.0399 | 1.1923
BICBase_SAC_hLoad_mHours | BICBase | CA CZ12 (Sacramento) | High | 75 | 49.6884 | 10.942 | 4.9093 | 15.7512 | 3.4686 | 1.5562
BICBase_SAC_lLoad_hHours | BICBase | CA CZ12 (Sacramento) | Low | 105 | 57.6145 | 29.1575 | 6.2684 | 18.2637 | 9.2429 | 1.9871
BICBase_SAC_lLoad_lHours | BICBase | CA CZ12 (Sacramento) | Low | 50 | 36.2275 | 10.8322 | 3.4185 | 11.4841 | 3.4338 | 1.0837
BICBase_SAC_lLoad_mHours | BICBase | CA CZ12 (Sacramento) | Low | 75 | 45.8361 | 18.7689 | 4.6685 | 14.53 | 5.9497 | 1.4799
BICBase_SAC_mLoad_hHours | BICBase | CA CZ12 (Sacramento) | Medium | 105 | 58.6862 | 23.4163 | 6.3266 | 18.6034 | 7.4229 | 2.0055
BICBase_SAC_mLoad_lHours | BICBase | CA CZ12 (Sacramento) | Medium | 50 | 37.9107 | 8.6812 | 3.5428 | 12.0176 | 2.7519 | 1.1231
BICBase_SAC_mLoad_mHours | BICBase | CA CZ12 (Sacramento) | Medium | 75 | 47.1897 | 14.9114 | 4.753 | 14.9591 | 4.7269 | 1.5067
BICBase_SF_hLoad_hHours | BICBase | CA CZ3 (San Francisco) | High | 105 | 41.5699 | 17.469 | 7.1301 | 13.1776 | 5.5376 | 2.2602
BICBase_SF_hLoad_lHours | BICBase | CA CZ3 (San Francisco) | High | 50 | 25.4064 | 4.5727 | 3.7069 | 8.0538 | 1.4495 | 1.1751
BICBase_SF_hLoad_mHours | BICBase | CA CZ3 (San Francisco) | High | 75 | 33.2067 | 9.5701 | 5.2392 | 10.5265 | 3.0337 | 1.6608
BICBase_SF_lLoad_hHours | BICBase | CA CZ3 (San Francisco) | Low | 105 | 40.5105 | 30.9558 | 7.0363 | 12.8418 | 9.8129 | 2.2305
BICBase_SF_lLoad_lHours | BICBase | CA CZ3 (San Francisco) | Low | 50 | 24.1636 | 9.1888 | 3.5596 | 7.6598 | 2.9128 | 1.1284
BICBase_SF_lLoad_mHours | BICBase | CA CZ3 (San Francisco) | Low | 75 | 32.0997 | 18.5001 | 5.129 | 10.1756 | 5.8645 | 1.6259
BICBase_SF_mLoad_hHours | BICBase | CA CZ3 (San Francisco) | Medium | 105 | 40.9003 | 24.6928 | 7.0715 | 12.9653 | 7.8276 | 2.2416
BICBase_SF_mLoad_lHours | BICBase | CA CZ3 (San Francisco) | Medium | 50 | 24.621 | 6.6701 | 3.612 | 7.8048 | 2.1144 | 1.145
BICBase_SF_mLoad_mHours | BICBase | CA CZ3 (San Francisco) | Medium | 75 | 32.5062 | 14.0971 | 5.1693 | 10.3044 | 4.4688 | 1.6387
BICMid_LA_hLoad_hHours | BICMid | CA CZ6 (LA) | High | 105 | 36.4583 | 0.11657 | 1.989 | 11.5572 | 0.036951 | 0.63051
BICMid_LA_hLoad_lHours | BICMid | CA CZ6 (LA) | High | 50 | 29.4155 | 0.030198 | 2.1338 | 9.3247 | 0.0095727 | 0.6764
BICMid_LA_hLoad_mHours | BICMid | CA CZ6 (LA) | High | 75 | 32.3012 | 0.076644 | 1.9982 | 10.2394 | 0.024296 | 0.63341
BICMid_LA_lLoad_hHours | BICMid | CA CZ6 (LA) | Low | 105 | 30.2536 | 0.94676 | 1.2915 | 9.5904 | 0.30012 | 0.4094
BICMid_LA_lLoad_lHours | BICMid | CA CZ6 (LA) | Low | 50 | 23.0787 | 0.17076 | 1.2715 | 7.3159 | 0.05413 | 0.40307
BICMid_LA_lLoad_mHours | BICMid | CA CZ6 (LA) | Low | 75 | 26.2225 | 0.43645 | 1.2471 | 8.3125 | 0.13835 | 0.39534
BICMid_LA_mLoad_hHours | BICMid | CA CZ6 (LA) | Medium | 105 | 32.5764 | 0.30132 | 1.5353 | 10.3267 | 0.095517 | 0.48669
BICMid_LA_mLoad_lHours | BICMid | CA CZ6 (LA) | Medium | 50 | 25.4049 | 0.075987 | 1.5657 | 8.0533 | 0.024088 | 0.49631
BICMid_LA_mLoad_mHours | BICMid | CA CZ6 (LA) | Medium | 75 | 28.4819 | 0.17969 | 1.5157 | 9.0287 | 0.056962 | 0.48048
BICMid_SAC_hLoad_hHours | BICMid | CA CZ12 (Sacramento) | High | 105 | 45.1446 | 3.6269 | 2.0263 | 14.3108 | 1.1497 | 0.64233
BICMid_SAC_hLoad_lHours | BICMid | CA CZ12 (Sacramento) | High | 50 | 34.8055 | 2.0115 | 2.3656 | 11.0333 | 0.63765 | 0.7499
BICMid_SAC_hLoad_mHours | BICMid | CA CZ12 (Sacramento) | High | 75 | 39.8657 | 2.9619 | 2.143 | 12.6374 | 0.93892 | 0.67932
BICMid_SAC_lLoad_hHours | BICMid | CA CZ12 (Sacramento) | Low | 105 | 38.6536 | 8.3583 | 1.3798 | 12.2531 | 2.6496 | 0.4374
BICMid_SAC_lLoad_lHours | BICMid | CA CZ12 (Sacramento) | Low | 50 | 29.0993 | 4.2016 | 1.5754 | 9.2244 | 1.3319 | 0.4994
BICMid_SAC_lLoad_mHours | BICMid | CA CZ12 (Sacramento) | Low | 75 | 33.8603 | 6.1786 | 1.4359 | 10.7337 | 1.9586 | 0.45517
BICMid_SAC_mLoad_hHours | BICMid | CA CZ12 (Sacramento) | Medium | 105 | 41.1598 | 5.7383 | 1.6141 | 13.0476 | 1.819 | 0.51166
BICMid_SAC_mLoad_lHours | BICMid | CA CZ12 (Sacramento) | Medium | 50 | 31.3601 | 3.072 | 1.8713 | 9.9411 | 0.97382 | 0.5932
BICMid_SAC_mLoad_mHours | BICMid | CA CZ12 (Sacramento) | Medium | 75 | 36.2607 | 4.5405 | 1.6968 | 11.4946 | 1.4393 | 0.5379
BICMid_SF_hLoad_hHours | BICMid | CA CZ3 (San Francisco) | High | 105 | 15.389 | 1.7415 | 2.6069 | 4.8783 | 0.55207 | 0.82638
BICMid_SF_hLoad_lHours | BICMid | CA CZ3 (San Francisco) | High | 50 | 12.2941 | 0.74301 | 2.5444 | 3.8972 | 0.23553 | 0.80657
BICMid_SF_hLoad_mHours | BICMid | CA CZ3 (San Francisco) | High | 75 | 13.8758 | 1.3009 | 2.5379 | 4.3986 | 0.41238 | 0.80453
BICMid_SF_lLoad_hHours | BICMid | CA CZ3 (San Francisco) | Low | 105 | 13.2044 | 4.5993 | 1.9116 | 4.1858 | 1.458 | 0.60597
BICMid_SF_lLoad_lHours | BICMid | CA CZ3 (San Francisco) | Low | 50 | 10.0407 | 1.8811 | 1.7137 | 3.1829 | 0.5963 | 0.54326
BICMid_SF_lLoad_mHours | BICMid | CA CZ3 (San Francisco) | Low | 75 | 11.7336 | 3.176 | 1.7938 | 3.7195 | 1.0068 | 0.56862
BICMid_SF_mLoad_hHours | BICMid | CA CZ3 (San Francisco) | Medium | 105 | 14.0308 | 3.0327 | 2.1557 | 4.4477 | 0.96137 | 0.68335
BICMid_SF_mLoad_lHours | BICMid | CA CZ3 (San Francisco) | Medium | 50 | 10.8521 | 1.2737 | 1.9949 | 3.4401 | 0.40375 | 0.63238
BICMid_SF_mLoad_mHours | BICMid | CA CZ3 (San Francisco) | Medium | 75 | 12.5199 | 2.1856 | 2.0494 | 3.9688 | 0.69283 | 0.64966
Guideline36_LA_hLoad_hHours | Guideline36 | CA CZ6 (LA) | High | 105 | 36.5573 | 0.066085 | 1.5506 | 11.5886 | 0.020949 | 0.49155
Guideline36_LA_hLoad_lHours | Guideline36 | CA CZ6 (LA) | High | 50 | 28.8076 | 0.024463 | 1.5241 | 9.132 | 0.0077546 | 0.48314
Guideline36_LA_hLoad_mHours | Guideline36 | CA CZ6 (LA) | High | 75 | 32.0279 | 0.043713 | 1.4635 | 10.1528 | 0.013857 | 0.46392
Guideline36_LA_lLoad_hHours | Guideline36 | CA CZ6 (LA) | Low | 105 | 30.4289 | 1.0236 | 1.0222 | 9.6459 | 0.32447 | 0.32402
Guideline36_LA_lLoad_lHours | Guideline36 | CA CZ6 (LA) | Low | 50 | 22.8151 | 0.12864 | 0.83849 | 7.2323 | 0.040777 | 0.2658
Guideline36_LA_lLoad_mHours | Guideline36 | CA CZ6 (LA) | Low | 75 | 26.1749 | 0.36378 | 0.89955 | 8.2974 | 0.11532 | 0.28516
Guideline36_LA_mLoad_hHours | Guideline36 | CA CZ6 (LA) | Medium | 105 | 32.7636 | 0.30247 | 1.1697 | 10.386 | 0.095883 | 0.37079
Guideline36_LA_mLoad_lHours | Guideline36 | CA CZ6 (LA) | Medium | 50 | 25.0022 | 0.05289 | 1.0361 | 7.9257 | 0.016766 | 0.32845
Guideline36_LA_mLoad_mHours | Guideline36 | CA CZ6 (LA) | Medium | 75 | 28.4562 | 0.12448 | 1.0606 | 9.0206 | 0.039459 | 0.3362
Guideline36_SAC_hLoad_hHours | Guideline36 | CA CZ12 (Sacramento) | High | 105 | 45.7656 | 2.9999 | 1.4403 | 14.5076 | 0.95095 | 0.45657
Guideline36_SAC_hLoad_lHours | Guideline36 | CA CZ12 (Sacramento) | High | 50 | 35.1199 | 1.6492 | 1.5541 | 11.1329 | 0.52279 | 0.49265
Guideline36_SAC_hLoad_mHours | Guideline36 | CA CZ12 (Sacramento) | High | 75 | 40.1449 | 2.439 | 1.4621 | 12.7259 | 0.77316 | 0.46347
Guideline36_SAC_lLoad_hHours | Guideline36 | CA CZ12 (Sacramento) | Low | 105 | 39.5252 | 7.1561 | 1.054 | 12.5294 | 2.2685 | 0.33411
Guideline36_SAC_lLoad_lHours | Guideline36 | CA CZ12 (Sacramento) | Low | 50 | 29.3213 | 3.3875 | 1.0095 | 9.2948 | 1.0738 | 0.32002
Guideline36_SAC_lLoad_mHours | Guideline36 | CA CZ12 (Sacramento) | Low | 75 | 34.2932 | 5.087 | 1.0085 | 10.8709 | 1.6126 | 0.31968
Guideline36_SAC_mLoad_hHours | Guideline36 | CA CZ12 (Sacramento) | Medium | 105 | 41.9848 | 4.8511 | 1.1829 | 13.3091 | 1.5378 | 0.37498
Guideline36_SAC_mLoad_lHours | Guideline36 | CA CZ12 (Sacramento) | Medium | 50 | 31.5587 | 2.5025 | 1.1969 | 10.0041 | 0.79328 | 0.37943
Guideline36_SAC_mLoad_mHours | Guideline36 | CA CZ12 (Sacramento) | Medium | 75 | 36.6523 | 3.7197 | 1.1619 | 11.6187 | 1.1792 | 0.36831
Guideline36_SF_hLoad_hHours | Guideline36 | CA CZ3 (San Francisco) | High | 105 | 15.5968 | 1.1334 | 2.1331 | 4.9442 | 0.35927 | 0.6762
Guideline36_SF_hLoad_lHours | Guideline36 | CA CZ3 (San Francisco) | High | 50 | 12.5628 | 0.5718 | 1.9284 | 3.9824 | 0.18126 | 0.61129
Guideline36_SF_hLoad_mHours | Guideline36 | CA CZ3 (San Francisco) | High | 75 | 13.9853 | 0.8896 | 1.9787 | 4.4333 | 0.282 | 0.62725
Guideline36_SF_lLoad_hHours | Guideline36 | CA CZ3 (San Francisco) | Low | 105 | 13.4952 | 3.3982 | 1.4562 | 4.278 | 1.0772 | 0.46163
Guideline36_SF_lLoad_lHours | Guideline36 | CA CZ3 (San Francisco) | Low | 50 | 10.1885 | 1.4591 | 1.1699 | 3.2297 | 0.46255 | 0.37084
Guideline36_SF_lLoad_mHours | Guideline36 | CA CZ3 (San Francisco) | Low | 75 | 11.8557 | 2.4179 | 1.3194 | 3.7582 | 0.76646 | 0.41826
Guideline36_SF_mLoad_hHours | Guideline36 | CA CZ3 (San Francisco) | Medium | 105 | 14.3364 | 2.1682 | 1.6447 | 4.5446 | 0.68731 | 0.52138
Guideline36_SF_mLoad_lHours | Guideline36 | CA CZ3 (San Francisco) | Medium | 50 | 11.0729 | 0.96091 | 1.3868 | 3.5101 | 0.30461 | 0.43962
Guideline36_SF_mLoad_mHours | Guideline36 | CA CZ3 (San Francisco) | Medium | 75 | 12.65 | 1.6183 | 1.5162 | 4.01 | 0.51301 | 0.48065

## Sheet1
| Control | Climate | Load | Hours | Ecoo (kWh/m2) | Ehea (kWh/m2) | Efan (kWh/m2)
A1B1C2_LA_hLoad_hHours | A1B1C2 | CA CZ6 (LA) | High | 105 | 56.1044 | 1.0822 | 4.1766
A1B1C2_LA_hLoad_lHours | A1B1C2 | CA CZ6 (LA) | High | 50 | 37.9401 | 0.13631 | 2.6647
A1B1C2_LA_hLoad_mHours | A1B1C2 | CA CZ6 (LA) | High | 75 | 45.5603 | 0.47354 | 3.2873
A1B1C2_LA_lLoad_hHours | A1B1C2 | CA CZ6 (LA) | Low | 105 | 50.805 | 7.0735 | 3.9122
A1B1C2_LA_lLoad_lHours | A1B1C2 | CA CZ6 (LA) | Low | 50 | 31.6511 | 0.99713 | 2.2001
A1B1C2_LA_lLoad_mHours | A1B1C2 | CA CZ6 (LA) | Low | 75 | 39.9446 | 3.1787 | 2.9478
A1B1C2_LA_mLoad_hHours | A1B1C2 | CA CZ6 (LA) | Medium | 105 | 52.6908 | 3.4378 | 3.9919
A1B1C2_LA_mLoad_lHours | A1B1C2 | CA CZ6 (LA) | Medium | 50 | 33.8625 | 0.40019 | 2.3505
A1B1C2_LA_mLoad_mHours | A1B1C2 | CA CZ6 (LA) | Medium | 75 | 42.0147 | 1.3973 | 3.0584
A1B1C2_SAC_hLoad_hHours | A1B1C2 | CA CZ12 (Sacramento) | High | 105 | 53.4638 | 8.4562 | 4.7167
A1B1C2_SAC_hLoad_lHours | A1B1C2 | CA CZ12 (Sacramento) | High | 50 | 38.4177 | 3.7938 | 3.1888
A1B1C2_SAC_hLoad_mHours | A1B1C2 | CA CZ12 (Sacramento) | High | 75 | 45.4439 | 6.0638 | 3.8132
A1B1C2_SAC_lLoad_hHours | A1B1C2 | CA CZ12 (Sacramento) | Low | 105 | 47.6135 | 16.3663 | 4.3535
A1B1C2_SAC_lLoad_lHours | A1B1C2 | CA CZ12 (Sacramento) | Low | 50 | 32.8803 | 7.0005 | 2.6691
A1B1C2_SAC_lLoad_mHours | A1B1C2 | CA CZ12 (Sacramento) | Low | 75 | 39.7496 | 11.0492 | 3.4065
A1B1C2_SAC_mLoad_hHours | A1B1C2 | CA CZ12 (Sacramento) | Medium | 105 | 49.7424 | 12.2225 | 4.4842
A1B1C2_SAC_mLoad_lHours | A1B1C2 | CA CZ12 (Sacramento) | Medium | 50 | 35.0295 | 5.4072 | 2.8551
A1B1C2_SAC_mLoad_mHours | A1B1C2 | CA CZ12 (Sacramento) | Medium | 75 | 41.9799 | 8.5179 | 3.5551
A1B1C2_SF_hLoad_hHours | A1B1C2 | CA CZ3 (San Francisco) | High | 105 | 32.041 | 6.9755 | 4.8697
A1B1C2_SF_hLoad_lHours | A1B1C2 | CA CZ3 (San Francisco) | High | 50 | 21.5479 | 2.289 | 2.8277
A1B1C2_SF_hLoad_mHours | A1B1C2 | CA CZ3 (San Francisco) | High | 75 | 26.5008 | 4.3356 | 3.7217
A1B1C2_SF_lLoad_hHours | A1B1C2 | CA CZ3 (San Francisco) | Low | 105 | 30.0762 | 15.5828 | 4.6796
A1B1C2_SF_lLoad_lHours | A1B1C2 | CA CZ3 (San Francisco) | Low | 50 | 19.1106 | 4.7353 | 2.5306
A1B1C2_SF_lLoad_mHours | A1B1C2 | CA CZ3 (San Francisco) | Low | 75 | 24.4417 | 9.1687 | 3.5001
A1B1C2_SF_mLoad_hHours | A1B1C2 | CA CZ3 (San Francisco) | Medium | 105 | 30.7723 | 10.9619 | 4.7454
A1B1C2_SF_mLoad_lHours | A1B1C2 | CA CZ3 (San Francisco) | Medium | 50 | 19.9222 | 3.4108 | 2.625
A1B1C2_SF_mLoad_mHours | A1B1C2 | CA CZ3 (San Francisco) | Medium | 75 | 25.1851 | 6.4558 | 3.5764
A1B2C1_LA_hLoad_hHours | A1B2C1 | CA CZ6 (LA) | High | 105 | 46.614 | 0.49196 | 6.2839
A1B2C1_LA_hLoad_lHours | A1B2C1 | CA CZ6 (LA) | High | 50 | 32.7434 | 0.061675 | 3.6104
A1B2C1_LA_hLoad_mHours | A1B2C1 | CA CZ6 (LA) | High | 75 | 38.9049 | 0.18035 | 4.765
A1B2C1_LA_lLoad_hHours | A1B2C1 | CA CZ6 (LA) | Low | 105 | 42.5315 | 4.9914 | 6.0485
A1B2C1_LA_lLoad_lHours | A1B2C1 | CA CZ6 (LA) | Low | 50 | 28.7201 | 0.46373 | 3.1935
A1B2C1_LA_lLoad_mHours | A1B2C1 | CA CZ6 (LA) | Low | 75 | 34.7874 | 2.1425 | 4.4746
A1B2C1_LA_mLoad_hHours | A1B2C1 | CA CZ6 (LA) | Medium | 105 | 43.8895 | 2.0015 | 6.13
A1B2C1_LA_mLoad_lHours | A1B2C1 | CA CZ6 (LA) | Medium | 50 | 30.3467 | 0.16394 | 3.3297
A1B2C1_LA_mLoad_mHours | A1B2C1 | CA CZ6 (LA) | Medium | 75 | 36.4227 | 0.62161 | 4.5704
A1B2C1_SAC_hLoad_hHours | A1B2C1 | CA CZ12 (Sacramento) | High | 105 | 51.8127 | 4.1143 | 6.6454
A1B2C1_SAC_hLoad_lHours | A1B2C1 | CA CZ12 (Sacramento) | High | 50 | 36.575 | 2.1288 | 3.9834
A1B2C1_SAC_hLoad_mHours | A1B2C1 | CA CZ12 (Sacramento) | High | 75 | 43.7747 | 3.1278 | 5.1291
A1B2C1_SAC_lLoad_hHours | A1B2C1 | CA CZ12 (Sacramento) | Low | 105 | 48.1842 | 11.9214 | 6.3802
A1B2C1_SAC_lLoad_lHours | A1B2C1 | CA CZ12 (Sacramento) | Low | 50 | 32.1553 | 4.6347 | 3.5474
A1B2C1_SAC_lLoad_mHours | A1B2C1 | CA CZ12 (Sacramento) | Low | 75 | 39.6406 | 7.8105 | 4.7944
A1B2C1_SAC_mLoad_hHours | A1B2C1 | CA CZ12 (Sacramento) | Medium | 105 | 49.3621 | 7.6515 | 6.4697
A1B2C1_SAC_mLoad_lHours | A1B2C1 | CA CZ12 (Sacramento) | Medium | 50 | 33.912 | 3.2754 | 3.7039
A1B2C1_SAC_mLoad_mHours | A1B2C1 | CA CZ12 (Sacramento) | Medium | 75 | 41.1193 | 5.0924 | 4.9124
A1B2C1_SF_hLoad_hHours | A1B2C1 | CA CZ3 (San Francisco) | High | 105 | 19.3105 | 2.6309 | 7.7949
A1B2C1_SF_hLoad_lHours | A1B2C1 | CA CZ3 (San Francisco) | High | 50 | 13.8646 | 1.0028 | 4.4804
A1B2C1_SF_hLoad_mHours | A1B2C1 | CA CZ3 (San Francisco) | High | 75 | 16.6947 | 1.8082 | 5.9395
A1B2C1_SF_lLoad_hHours | A1B2C1 | CA CZ3 (San Francisco) | Low | 105 | 18.1536 | 7.6094 | 7.5058
A1B2C1_SF_lLoad_lHours | A1B2C1 | CA CZ3 (San Francisco) | Low | 50 | 12.5885 | 2.378 | 4.0507
A1B2C1_SF_lLoad_mHours | A1B2C1 | CA CZ3 (San Francisco) | Low | 75 | 15.5346 | 4.4667 | 5.6179
A1B2C1_SF_mLoad_hHours | A1B2C1 | CA CZ3 (San Francisco) | Medium | 105 | 18.5763 | 4.6058 | 7.6165
A1B2C1_SF_mLoad_lHours | A1B2C1 | CA CZ3 (San Francisco) | Medium | 50 | 13.0627 | 1.6526 | 4.1932
A1B2C1_SF_mLoad_mHours | A1B2C1 | CA CZ3 (San Francisco) | Medium | 75 | 15.972 | 2.8886 | 5.7341
A1B2C2_LA_hLoad_hHours | A1B2C2 | CA CZ6 (LA) | High | 105 | 40.0796 | 0.094052 | 4.7493
A1B2C2_LA_hLoad_lHours | A1B2C2 | CA CZ6 (LA) | High | 50 | 30.9355 | 0.02467 | 3.2338
A1B2C2_LA_hLoad_mHours | A1B2C2 | CA CZ6 (LA) | High | 75 | 34.7889 | 0.063288 | 3.8678
A1B2C2_LA_lLoad_hHours | A1B2C2 | CA CZ6 (LA) | Low | 105 | 34.3407 | 0.97269 | 4.155
A1B2C2_LA_lLoad_lHours | A1B2C2 | CA CZ6 (LA) | Low | 50 | 24.8746 | 0.15372 | 2.4578
A1B2C2_LA_lLoad_mHours | A1B2C2 | CA CZ6 (LA) | Low | 75 | 29.0411 | 0.38515 | 3.208
A1B2C2_LA_mLoad_hHours | A1B2C2 | CA CZ6 (LA) | Medium | 105 | 36.4643 | 0.24674 | 4.3289
A1B2C2_LA_mLoad_lHours | A1B2C2 | CA CZ6 (LA) | Medium | 50 | 27.0228 | 0.06629 | 2.692
A1B2C2_LA_mLoad_mHours | A1B2C2 | CA CZ6 (LA) | Medium | 75 | 31.1943 | 0.1494 | 3.4128
A1B2C2_SAC_hLoad_hHours | A1B2C2 | CA CZ12 (Sacramento) | High | 105 | 47.4814 | 3.1406 | 5.0045
A1B2C2_SAC_hLoad_lHours | A1B2C2 | CA CZ12 (Sacramento) | High | 50 | 35.5046 | 1.8254 | 3.4672
A1B2C2_SAC_hLoad_mHours | A1B2C2 | CA CZ12 (Sacramento) | High | 75 | 41.2734 | 2.6377 | 4.1064
A1B2C2_SAC_lLoad_hHours | A1B2C2 | CA CZ12 (Sacramento) | Low | 105 | 41.436 | 7.7155 | 4.5092
A1B2C2_SAC_lLoad_lHours | A1B2C2 | CA CZ12 (Sacramento) | Low | 50 | 30.0461 | 3.9075 | 2.8186
A1B2C2_SAC_lLoad_mHours | A1B2C2 | CA CZ12 (Sacramento) | Low | 75 | 35.6203 | 5.6754 | 3.5651
A1B2C2_SAC_mLoad_hHours | A1B2C2 | CA CZ12 (Sacramento) | Medium | 105 | 43.7202 | 5.0786 | 4.6853
A1B2C2_SAC_mLoad_lHours | A1B2C2 | CA CZ12 (Sacramento) | Medium | 50 | 32.1942 | 2.8321 | 3.0464
A1B2C2_SAC_mLoad_mHours | A1B2C2 | CA CZ12 (Sacramento) | Medium | 75 | 37.8788 | 4.1062 | 3.7554
A1B2C2_SF_hLoad_hHours | A1B2C2 | CA CZ3 (San Francisco) | High | 105 | 16.7217 | 1.512 | 5.7993
A1B2C2_SF_hLoad_lHours | A1B2C2 | CA CZ3 (San Francisco) | High | 50 | 12.9347 | 0.67432 | 3.8374
A1B2C2_SF_hLoad_mHours | A1B2C2 | CA CZ3 (San Francisco) | High | 75 | 14.8759 | 1.1544 | 4.7058
A1B2C2_SF_lLoad_hHours | A1B2C2 | CA CZ3 (San Francisco) | Low | 105 | 14.7714 | 4.1107 | 5.2374
A1B2C2_SF_lLoad_lHours | A1B2C2 | CA CZ3 (San Francisco) | Low | 50 | 10.8171 | 1.7386 | 3.0843
A1B2C2_SF_lLoad_mHours | A1B2C2 | CA CZ3 (San Francisco) | Low | 75 | 12.9235 | 2.8839 | 4.065
A1B2C2_SF_mLoad_hHours | A1B2C2 | CA CZ3 (San Francisco) | Medium | 105 | 15.5026 | 2.6665 | 5.409
A1B2C2_SF_mLoad_lHours | A1B2C2 | CA CZ3 (San Francisco) | Medium | 50 | 11.547 | 1.17 | 3.3123
A1B2C2_SF_mLoad_mHours | A1B2C2 | CA CZ3 (San Francisco) | Medium | 75 | 13.6261 | 1.9707 | 4.2519
A2B1C1_LA_hLoad_hHours | A2B1C1 | CA CZ6 (LA) | High | 105 | 61.8151 | 6.0742 | 1.8189
A2B1C1_LA_hLoad_lHours | A2B1C1 | CA CZ6 (LA) | High | 50 | 39.0431 | 0.64074 | 1.6031
A2B1C1_LA_hLoad_mHours | A2B1C1 | CA CZ6 (LA) | High | 75 | 48.8751 | 2.371 | 1.6128
A2B1C1_LA_lLoad_hHours | A2B1C1 | CA CZ6 (LA) | Low | 105 | 58.0987 | 17.2066 | 1.5901
A2B1C1_LA_lLoad_lHours | A2B1C1 | CA CZ6 (LA) | Low | 50 | 34.6765 | 3.2746 | 1.1766
A2B1C1_LA_lLoad_mHours | A2B1C1 | CA CZ6 (LA) | Low | 75 | 44.8086 | 9.054 | 1.3198
A2B1C1_LA_mLoad_hHours | A2B1C1 | CA CZ6 (LA) | Medium | 105 | 59.355 | 11.6263 | 1.6687
A2B1C1_LA_mLoad_lHours | A2B1C1 | CA CZ6 (LA) | Medium | 50 | 36.3808 | 1.624 | 1.3244
A2B1C1_LA_mLoad_mHours | A2B1C1 | CA CZ6 (LA) | Medium | 75 | 46.2444 | 5.3682 | 1.4195
A2B1C1_SAC_hLoad_hHours | A2B1C1 | CA CZ12 (Sacramento) | High | 105 | 55.6322 | 16.4858 | 2.0908
A2B1C1_SAC_hLoad_lHours | A2B1C1 | CA CZ12 (Sacramento) | High | 50 | 38.8023 | 6.3357 | 2.1492
A2B1C1_SAC_hLoad_mHours | A2B1C1 | CA CZ12 (Sacramento) | High | 75 | 46.4547 | 10.7171 | 2.034
A2B1C1_SAC_lLoad_hHours | A2B1C1 | CA CZ12 (Sacramento) | Low | 105 | 51.9125 | 28.1469 | 1.7621
A2B1C1_SAC_lLoad_lHours | A2B1C1 | CA CZ12 (Sacramento) | Low | 50 | 34.1751 | 10.5864 | 1.6134
A2B1C1_SAC_lLoad_mHours | A2B1C1 | CA CZ12 (Sacramento) | Low | 75 | 42.1469 | 18.2004 | 1.6137
A2B1C1_SAC_mLoad_hHours | A2B1C1 | CA CZ12 (Sacramento) | Medium | 105 | 53.1475 | 22.5471 | 1.8769
A2B1C1_SAC_mLoad_lHours | A2B1C1 | CA CZ12 (Sacramento) | Medium | 50 | 35.9908 | 8.5136 | 1.8143
A2B1C1_SAC_mLoad_mHours | A2B1C1 | CA CZ12 (Sacramento) | Medium | 75 | 43.6855 | 14.4867 | 1.765
A2B1C1_SF_hLoad_hHours | A2B1C1 | CA CZ3 (San Francisco) | High | 105 | 34.8292 | 16.3297 | 2.2123
A2B1C1_SF_hLoad_lHours | A2B1C1 | CA CZ3 (San Francisco) | High | 50 | 22.4948 | 4.3983 | 1.6279
A2B1C1_SF_hLoad_mHours | A2B1C1 | CA CZ3 (San Francisco) | High | 75 | 28.4514 | 9.0285 | 1.8495
A2B1C1_SF_lLoad_hHours | A2B1C1 | CA CZ3 (San Francisco) | Low | 105 | 33.5689 | 29.3579 | 2.0249
A2B1C1_SF_lLoad_lHours | A2B1C1 | CA CZ3 (San Francisco) | Low | 50 | 20.9778 | 8.7077 | 1.3538
A2B1C1_SF_lLoad_mHours | A2B1C1 | CA CZ3 (San Francisco) | Low | 75 | 27.1234 | 17.5178 | 1.6333
A2B1C1_SF_mLoad_hHours | A2B1C1 | CA CZ3 (San Francisco) | Medium | 105 | 34.0247 | 23.2039 | 2.0936
A2B1C1_SF_mLoad_lHours | A2B1C1 | CA CZ3 (San Francisco) | Medium | 50 | 21.5422 | 6.3578 | 1.4537
A2B1C1_SF_mLoad_mHours | A2B1C1 | CA CZ3 (San Francisco) | Medium | 75 | 27.6018 | 13.2506 | 1.7118
A2B1C2_LA_hLoad_hHours | A2B1C2 | CA CZ6 (LA) | High | 105 | 49.7159 | 0.80396 | 1.2701
A2B1C2_LA_hLoad_lHours | A2B1C2 | CA CZ6 (LA) | High | 50 | 35.5216 | 0.11594 | 1.42
A2B1C2_LA_hLoad_mHours | A2B1C2 | CA CZ6 (LA) | High | 75 | 41.4489 | 0.38167 | 1.2645
A2B1C2_LA_lLoad_hHours | A2B1C2 | CA CZ6 (LA) | Low | 105 | 43.9179 | 5.8303 | 0.9243
A2B1C2_LA_lLoad_lHours | A2B1C2 | CA CZ6 (LA) | Low | 50 | 28.7739 | 0.82438 | 0.87737
A2B1C2_LA_lLoad_mHours | A2B1C2 | CA CZ6 (LA) | Low | 75 | 35.2305 | 2.6027 | 0.8523
A2B1C2_LA_mLoad_hHours | A2B1C2 | CA CZ6 (LA) | Medium | 105 | 45.9337 | 2.6377 | 1.0372
A2B1C2_LA_mLoad_lHours | A2B1C2 | CA CZ6 (LA) | Medium | 50 | 31.1991 | 0.33286 | 1.0684
A2B1C2_LA_mLoad_mHours | A2B1C2 | CA CZ6 (LA) | Medium | 75 | 37.4984 | 1.1174 | 0.9946
A2B1C2_SAC_hLoad_hHours | A2B1C2 | CA CZ12 (Sacramento) | High | 105 | 49.6763 | 8.044 | 1.5916
A2B1C2_SAC_hLoad_lHours | A2B1C2 | CA CZ12 (Sacramento) | High | 50 | 37.1288 | 3.6553 | 1.9622
A2B1C2_SAC_hLoad_mHours | A2B1C2 | CA CZ12 (Sacramento) | High | 75 | 43.0827 | 5.8204 | 1.6981
A2B1C2_SAC_lLoad_hHours | A2B1C2 | CA CZ12 (Sacramento) | Low | 105 | 43.3757 | 15.4228 | 1.1512
A2B1C2_SAC_lLoad_lHours | A2B1C2 | CA CZ12 (Sacramento) | Low | 50 | 31.3156 | 6.7534 | 1.3322
A2B1C2_SAC_lLoad_mHours | A2B1C2 | CA CZ12 (Sacramento) | Low | 75 | 37.0192 | 10.5661 | 1.1824
A2B1C2_SAC_mLoad_hHours | A2B1C2 | CA CZ12 (Sacramento) | Medium | 105 | 45.7122 | 11.5379 | 1.3088
A2B1C2_SAC_mLoad_lHours | A2B1C2 | CA CZ12 (Sacramento) | Medium | 50 | 33.5888 | 5.21 | 1.5684
A2B1C2_SAC_mLoad_mHours | A2B1C2 | CA CZ12 (Sacramento) | Medium | 75 | 39.3949 | 8.175 | 1.3732
A2B1C2_SF_hLoad_hHours | A2B1C2 | CA CZ3 (San Francisco) | High | 105 | 27.2422 | 6.3802 | 1.3979
A2B1C2_SF_hLoad_lHours | A2B1C2 | CA CZ3 (San Francisco) | High | 50 | 19.479 | 2.1569 | 1.2814
A2B1C2_SF_hLoad_mHours | A2B1C2 | CA CZ3 (San Francisco) | High | 75 | 23.1465 | 4.0376 | 1.2875
A2B1C2_SF_lLoad_hHours | A2B1C2 | CA CZ3 (San Francisco) | Low | 105 | 24.9694 | 14.1704 | 1.1437
A2B1C2_SF_lLoad_lHours | A2B1C2 | CA CZ3 (San Francisco) | Low | 50 | 16.7719 | 4.4523 | 0.92359
A2B1C2_SF_lLoad_mHours | A2B1C2 | CA CZ3 (San Francisco) | Low | 75 | 20.7727 | 8.4086 | 0.99922
A2B1C2_SF_mLoad_hHours | A2B1C2 | CA CZ3 (San Francisco) | Medium | 105 | 25.76 | 9.9007 | 1.232
A2B1C2_SF_mLoad_lHours | A2B1C2 | CA CZ3 (San Francisco) | Medium | 50 | 17.679 | 3.2162 | 1.0465
A2B1C2_SF_mLoad_mHours | A2B1C2 | CA CZ3 (San Francisco) | Medium | 75 | 21.6309 | 5.9868 | 1.1009
A2B2C1_LA_hLoad_hHours | A2B2C1 | CA CZ6 (LA) | High | 105 | 41.7378 | 0.51828 | 2.4925
A2B2C1_LA_hLoad_lHours | A2B2C1 | CA CZ6 (LA) | High | 50 | 30.835 | 0.074494 | 2.2952
A2B2C1_LA_hLoad_mHours | A2B2C1 | CA CZ6 (LA) | High | 75 | 35.5823 | 0.22372 | 2.3325
A2B2C1_LA_lLoad_hHours | A2B2C1 | CA CZ6 (LA) | Low | 105 | 37.3527 | 4.9803 | 1.9546
A2B2C1_LA_lLoad_lHours | A2B2C1 | CA CZ6 (LA) | Low | 50 | 26.3654 | 0.48853 | 1.5827
A2B2C1_LA_lLoad_mHours | A2B2C1 | CA CZ6 (LA) | Low | 75 | 31.081 | 2.1012 | 1.7202
A2B2C1_LA_mLoad_hHours | A2B2C1 | CA CZ6 (LA) | Medium | 105 | 38.8218 | 2.009 | 2.145
A2B2C1_LA_mLoad_lHours | A2B2C1 | CA CZ6 (LA) | Medium | 50 | 28.1278 | 0.18949 | 1.8459
A2B2C1_LA_mLoad_mHours | A2B2C1 | CA CZ6 (LA) | Medium | 75 | 32.8476 | 0.63036 | 1.9377
A2B2C1_SAC_hLoad_hHours | A2B2C1 | CA CZ12 (Sacramento) | High | 105 | 48.6183 | 4.7426 | 2.5424
A2B2C1_SAC_hLoad_lHours | A2B2C1 | CA CZ12 (Sacramento) | High | 50 | 35.6958 | 2.398 | 2.5771
A2B2C1_SAC_hLoad_mHours | A2B2C1 | CA CZ12 (Sacramento) | High | 75 | 41.8981 | 3.6019 | 2.5015
A2B2C1_SAC_lLoad_hHours | A2B2C1 | CA CZ12 (Sacramento) | Low | 105 | 44.458 | 12.6819 | 2.0002
A2B2C1_SAC_lLoad_lHours | A2B2C1 | CA CZ12 (Sacramento) | Low | 50 | 30.9375 | 5.0488 | 1.8829
A2B2C1_SAC_lLoad_mHours | A2B2C1 | CA CZ12 (Sacramento) | Low | 75 | 37.2955 | 8.3865 | 1.8876
A2B2C1_SAC_mLoad_hHours | A2B2C1 | CA CZ12 (Sacramento) | Medium | 105 | 45.8603 | 8.4191 | 2.1903
A2B2C1_SAC_mLoad_lHours | A2B2C1 | CA CZ12 (Sacramento) | Medium | 50 | 32.8388 | 3.6322 | 2.1436
A2B2C1_SAC_mLoad_mHours | A2B2C1 | CA CZ12 (Sacramento) | Medium | 75 | 38.9752 | 5.6572 | 2.1109
A2B2C1_SF_hLoad_hHours | A2B2C1 | CA CZ3 (San Francisco) | High | 105 | 17.4312 | 3.1402 | 3.4085
A2B2C1_SF_hLoad_lHours | A2B2C1 | CA CZ3 (San Francisco) | High | 50 | 13.047 | 1.1432 | 2.8671
A2B2C1_SF_hLoad_mHours | A2B2C1 | CA CZ3 (San Francisco) | High | 75 | 15.3261 | 2.1062 | 3.0774
A2B2C1_SF_lLoad_hHours | A2B2C1 | CA CZ3 (San Francisco) | Low | 105 | 16.0601 | 8.6438 | 2.8469
A2B2C1_SF_lLoad_lHours | A2B2C1 | CA CZ3 (San Francisco) | Low | 50 | 11.5572 | 2.6348 | 2.2134
A2B2C1_SF_lLoad_mHours | A2B2C1 | CA CZ3 (San Francisco) | Low | 75 | 13.9349 | 5.0135 | 2.4945
A2B2C1_SF_mLoad_hHours | A2B2C1 | CA CZ3 (San Francisco) | Medium | 105 | 16.5613 | 5.3733 | 3.0579
A2B2C1_SF_mLoad_lHours | A2B2C1 | CA CZ3 (San Francisco) | Medium | 50 | 12.1152 | 1.8501 | 2.449
A2B2C1_SF_mLoad_mHours | A2B2C1 | CA CZ3 (San Francisco) | Medium | 75 | 14.4589 | 3.3045 | 2.7091
BICBase_LA_hLoad_hHours | BICBase | CA CZ6 (LA) | High | 105 | 70.4728 | 7.1509 | 5.977
BICBase_LA_hLoad_lHours | BICBase | CA CZ6 (LA) | High | 50 | 42.4189 | 0.73941 | 3.2269
BICBase_LA_hLoad_mHours | BICBase | CA CZ6 (LA) | High | 75 | 54.7306 | 2.7878 | 4.4187
BICBase_LA_lLoad_hHours | BICBase | CA CZ6 (LA) | Low | 105 | 66.9565 | 18.9273 | 5.8779
BICBase_LA_lLoad_lHours | BICBase | CA CZ6 (LA) | Low | 50 | 38.4749 | 3.6996 | 3.0001
BICBase_LA_lLoad_mHours | BICBase | CA CZ6 (LA) | Low | 75 | 50.9588 | 10.0547 | 4.2859
BICBase_LA_mLoad_hHours | BICBase | CA CZ6 (LA) | Medium | 105 | 68.1344 | 13.1876 | 5.9126
BICBase_LA_mLoad_lHours | BICBase | CA CZ6 (LA) | Medium | 50 | 40.0972 | 1.8673 | 3.0735
BICBase_LA_mLoad_mHours | BICBase | CA CZ6 (LA) | Medium | 75 | 52.239 | 6.157 | 4.3306
BICBase_SAC_hLoad_hHours | BICBase | CA CZ12 (Sacramento) | High | 105 | 60.8761 | 17.0616 | 6.4408
BICBase_SAC_hLoad_lHours | BICBase | CA CZ12 (Sacramento) | High | 50 | 40.5151 | 6.4352 | 3.7611
BICBase_SAC_hLoad_mHours | BICBase | CA CZ12 (Sacramento) | High | 75 | 49.6884 | 10.942 | 4.9093
BICBase_SAC_lLoad_hHours | BICBase | CA CZ12 (Sacramento) | Low | 105 | 57.6145 | 29.1575 | 6.2684
BICBase_SAC_lLoad_lHours | BICBase | CA CZ12 (Sacramento) | Low | 50 | 36.2275 | 10.8322 | 3.4185
BICBase_SAC_lLoad_mHours | BICBase | CA CZ12 (Sacramento) | Low | 75 | 45.8361 | 18.7689 | 4.6685
BICBase_SAC_mLoad_hHours | BICBase | CA CZ12 (Sacramento) | Medium | 105 | 58.6862 | 23.4163 | 6.3266
BICBase_SAC_mLoad_lHours | BICBase | CA CZ12 (Sacramento) | Medium | 50 | 37.9107 | 8.6812 | 3.5428
BICBase_SAC_mLoad_mHours | BICBase | CA CZ12 (Sacramento) | Medium | 75 | 47.1897 | 14.9114 | 4.753
BICBase_SF_hLoad_hHours | BICBase | CA CZ3 (San Francisco) | High | 105 | 41.5699 | 17.469 | 7.1301
BICBase_SF_hLoad_lHours | BICBase | CA CZ3 (San Francisco) | High | 50 | 25.4064 | 4.5727 | 3.7069
BICBase_SF_hLoad_mHours | BICBase | CA CZ3 (San Francisco) | High | 75 | 33.2067 | 9.5701 | 5.2392
BICBase_SF_lLoad_hHours | BICBase | CA CZ3 (San Francisco) | Low | 105 | 40.5105 | 30.9558 | 7.0363
BICBase_SF_lLoad_lHours | BICBase | CA CZ3 (San Francisco) | Low | 50 | 24.1636 | 9.1888 | 3.5596
BICBase_SF_lLoad_mHours | BICBase | CA CZ3 (San Francisco) | Low | 75 | 32.0997 | 18.5001 | 5.129
BICBase_SF_mLoad_hHours | BICBase | CA CZ3 (San Francisco) | Medium | 105 | 40.9003 | 24.6928 | 7.0715
BICBase_SF_mLoad_lHours | BICBase | CA CZ3 (San Francisco) | Medium | 50 | 24.621 | 6.6701 | 3.612
BICBase_SF_mLoad_mHours | BICBase | CA CZ3 (San Francisco) | Medium | 75 | 32.5062 | 14.0971 | 5.1693
BICMid_LA_hLoad_hHours | BICMid | CA CZ6 (LA) | High | 105 | 36.4583 | 0.11657 | 1.989
BICMid_LA_hLoad_lHours | BICMid | CA CZ6 (LA) | High | 50 | 29.4155 | 0.030198 | 2.1338
BICMid_LA_hLoad_mHours | BICMid | CA CZ6 (LA) | High | 75 | 32.3012 | 0.076644 | 1.9982
BICMid_LA_lLoad_hHours | BICMid | CA CZ6 (LA) | Low | 105 | 30.2536 | 0.94676 | 1.2915
BICMid_LA_lLoad_lHours | BICMid | CA CZ6 (LA) | Low | 50 | 23.0787 | 0.17076 | 1.2715
BICMid_LA_lLoad_mHours | BICMid | CA CZ6 (LA) | Low | 75 | 26.2225 | 0.43645 | 1.2471
BICMid_LA_mLoad_hHours | BICMid | CA CZ6 (LA) | Medium | 105 | 32.5764 | 0.30132 | 1.5353
BICMid_LA_mLoad_lHours | BICMid | CA CZ6 (LA) | Medium | 50 | 25.4049 | 0.075987 | 1.5657
BICMid_LA_mLoad_mHours | BICMid | CA CZ6 (LA) | Medium | 75 | 28.4819 | 0.17969 | 1.5157
BICMid_SAC_hLoad_hHours | BICMid | CA CZ12 (Sacramento) | High | 105 | 45.1446 | 3.6269 | 2.0263
BICMid_SAC_hLoad_lHours | BICMid | CA CZ12 (Sacramento) | High | 50 | 34.8055 | 2.0115 | 2.3656
BICMid_SAC_hLoad_mHours | BICMid | CA CZ12 (Sacramento) | High | 75 | 39.8657 | 2.9619 | 2.143
BICMid_SAC_lLoad_hHours | BICMid | CA CZ12 (Sacramento) | Low | 105 | 38.6536 | 8.3583 | 1.3798
BICMid_SAC_lLoad_lHours | BICMid | CA CZ12 (Sacramento) | Low | 50 | 29.0993 | 4.2016 | 1.5754
BICMid_SAC_lLoad_mHours | BICMid | CA CZ12 (Sacramento) | Low | 75 | 33.8603 | 6.1786 | 1.4359
BICMid_SAC_mLoad_hHours | BICMid | CA CZ12 (Sacramento) | Medium | 105 | 41.1598 | 5.7383 | 1.6141
BICMid_SAC_mLoad_lHours | BICMid | CA CZ12 (Sacramento) | Medium | 50 | 31.3601 | 3.072 | 1.8713
BICMid_SAC_mLoad_mHours | BICMid | CA CZ12 (Sacramento) | Medium | 75 | 36.2607 | 4.5405 | 1.6968
BICMid_SF_hLoad_hHours | BICMid | CA CZ3 (San Francisco) | High | 105 | 15.389 | 1.7415 | 2.6069
BICMid_SF_hLoad_lHours | BICMid | CA CZ3 (San Francisco) | High | 50 | 12.2941 | 0.74301 | 2.5444
BICMid_SF_hLoad_mHours | BICMid | CA CZ3 (San Francisco) | High | 75 | 13.8758 | 1.3009 | 2.5379
BICMid_SF_lLoad_hHours | BICMid | CA CZ3 (San Francisco) | Low | 105 | 13.2044 | 4.5993 | 1.9116
BICMid_SF_lLoad_lHours | BICMid | CA CZ3 (San Francisco) | Low | 50 | 10.0407 | 1.8811 | 1.7137
BICMid_SF_lLoad_mHours | BICMid | CA CZ3 (San Francisco) | Low | 75 | 11.7336 | 3.176 | 1.7938
BICMid_SF_mLoad_hHours | BICMid | CA CZ3 (San Francisco) | Medium | 105 | 14.0308 | 3.0327 | 2.1557
BICMid_SF_mLoad_lHours | BICMid | CA CZ3 (San Francisco) | Medium | 50 | 10.8521 | 1.2737 | 1.9949
BICMid_SF_mLoad_mHours | BICMid | CA CZ3 (San Francisco) | Medium | 75 | 12.5199 | 2.1856 | 2.0494
Guideline36_LA_hLoad_hHours | Guideline36 | CA CZ6 (LA) | High | 105 | 36.5573 | 0.066085 | 1.5506
Guideline36_LA_hLoad_lHours | Guideline36 | CA CZ6 (LA) | High | 50 | 28.8076 | 0.024463 | 1.5241
Guideline36_LA_hLoad_mHours | Guideline36 | CA CZ6 (LA) | High | 75 | 32.0279 | 0.043713 | 1.4635
Guideline36_LA_lLoad_hHours | Guideline36 | CA CZ6 (LA) | Low | 105 | 30.4289 | 1.0236 | 1.0222
Guideline36_LA_lLoad_lHours | Guideline36 | CA CZ6 (LA) | Low | 50 | 22.8151 | 0.12864 | 0.83849
Guideline36_LA_lLoad_mHours | Guideline36 | CA CZ6 (LA) | Low | 75 | 26.1749 | 0.36378 | 0.89955
Guideline36_LA_mLoad_hHours | Guideline36 | CA CZ6 (LA) | Medium | 105 | 32.7636 | 0.30247 | 1.1697
Guideline36_LA_mLoad_lHours | Guideline36 | CA CZ6 (LA) | Medium | 50 | 25.0022 | 0.05289 | 1.0361
Guideline36_LA_mLoad_mHours | Guideline36 | CA CZ6 (LA) | Medium | 75 | 28.4562 | 0.12448 | 1.0606
Guideline36_SAC_hLoad_hHours | Guideline36 | CA CZ12 (Sacramento) | High | 105 | 45.7656 | 2.9999 | 1.4403
Guideline36_SAC_hLoad_lHours | Guideline36 | CA CZ12 (Sacramento) | High | 50 | 35.1199 | 1.6492 | 1.5541
Guideline36_SAC_hLoad_mHours | Guideline36 | CA CZ12 (Sacramento) | High | 75 | 40.1449 | 2.439 | 1.4621
Guideline36_SAC_lLoad_hHours | Guideline36 | CA CZ12 (Sacramento) | Low | 105 | 39.5252 | 7.1561 | 1.054
Guideline36_SAC_lLoad_lHours | Guideline36 | CA CZ12 (Sacramento) | Low | 50 | 29.3213 | 3.3875 | 1.0095
Guideline36_SAC_lLoad_mHours | Guideline36 | CA CZ12 (Sacramento) | Low | 75 | 34.2932 | 5.087 | 1.0085
Guideline36_SAC_mLoad_hHours | Guideline36 | CA CZ12 (Sacramento) | Medium | 105 | 41.9848 | 4.8511 | 1.1829
Guideline36_SAC_mLoad_lHours | Guideline36 | CA CZ12 (Sacramento) | Medium | 50 | 31.5587 | 2.5025 | 1.1969
Guideline36_SAC_mLoad_mHours | Guideline36 | CA CZ12 (Sacramento) | Medium | 75 | 36.6523 | 3.7197 | 1.1619
Guideline36_SF_hLoad_hHours | Guideline36 | CA CZ3 (San Francisco) | High | 105 | 15.5968 | 1.1334 | 2.1331
Guideline36_SF_hLoad_lHours | Guideline36 | CA CZ3 (San Francisco) | High | 50 | 12.5628 | 0.5718 | 1.9284
Guideline36_SF_hLoad_mHours | Guideline36 | CA CZ3 (San Francisco) | High | 75 | 13.9853 | 0.8896 | 1.9787
Guideline36_SF_lLoad_hHours | Guideline36 | CA CZ3 (San Francisco) | Low | 105 | 13.4952 | 3.3982 | 1.4562
Guideline36_SF_lLoad_lHours | Guideline36 | CA CZ3 (San Francisco) | Low | 50 | 10.1885 | 1.4591 | 1.1699
Guideline36_SF_lLoad_mHours | Guideline36 | CA CZ3 (San Francisco) | Low | 75 | 11.8557 | 2.4179 | 1.3194
Guideline36_SF_mLoad_hHours | Guideline36 | CA CZ3 (San Francisco) | Medium | 105 | 14.3364 | 2.1682 | 1.6447
Guideline36_SF_mLoad_lHours | Guideline36 | CA CZ3 (San Francisco) | Medium | 50 | 11.0729 | 0.96091 | 1.3868
Guideline36_SF_mLoad_mHours | Guideline36 | CA CZ3 (San Francisco) | Medium | 75 | 12.65 | 1.6183 | 1.5162

## controls
SI |  | DSP Setpoint | SAT Setpoint | VAV Ctrl
| primary | Fixed | Fixed | Single Max (30%) | BICBase
| A2B2C1 | Limiting Reset | OAT Reset | Single Max (20%) | BICMid
|  | Fixed | Fixed | Single Max (20%) | A1B1C2
| secondary | Limiting Reset | Fixed | Single Max (30%) | A2B1C1
| A1B1C2 | Limiting Reset | Fixed | Single Max (20%) | A2B1C2
|  | Fixed | OAT Reset | Single Max (30%) | A1B2C1
|  | Fixed | OAT Reset | Single Max (20%) | A1B2C2
|  | Limiting Reset | OAT Reset | Single Max (30%) | A2B2C1
|  | T&R Reset | T&R Reset | Dual Max | Guideline36
IP
primary
A2B1C1
secondary
BICBase

## factors
Type | Measure/Factors | Description
Explicit Modeling
Building | Building space type | Start with office with a "typical" blend of space types (private office, open office, conference, etc), consider classroom and other building types in future
| Window to wall ratio | Assume 40% or whatever is in medium office model. Consider high, medium, low for future refinement (80, 60, 40%)?
| Envelope properties | Assume modern construction. Consider current code vs ~<1990 for future refinement
| Perimeter vs interior | Consider this as factor for future, e.g. middle story in high rise (low envelope exposure) vs single story (high envelope exposure)
Usage | Schedule (hr/wk) | High, medium, low number of hours per week of system operation: 100 (e.g. 6 am to 10 pm M-F, 8 am to 6 pm SS), 75 (e.g. 8 am to 8 pm M-F), 50 (e.g. 8 am to 6 pm M-F), consider expanding to 24/7 in future
| Load Magnitude | Assume "typical" design internal gains and stochastic occupancy profiles. One option is high, medium, low load magnitude perhaps based on scalar adjustment of internal gain schedules. This would not account for load variability (e.g. constant load vs highly variable). Or another option is to model "high" as low variability, and "low" with increased variability. Assume lighting goes to zero in empty rooms for private office and conference rooms, stays at design for open office. Assume plug loads reduce with occupancy.
| Lighting occupancy sensors | Assume use of occupancy sensors. Consider including option to exclude this in future.
HVAC / BAS | HVAC System Type | Only model VAV reheat for now, with DX cooling. Account for CHW vs DX based on simple annual cooling efficiency from user input. Consider adding other system types in future.
| SAT Setpoint Reset | Fixed 55, linear reset from 55 to 65 for OATs from 70 to 60 (?), demand based reset per G36
| DSP Setpoint Reset | Fixed setpoint, limiting (does this end up very different from T&R in modeling?), demand based reset per G36
| Fan power | Consider adding high vs low based on W/cfm in future
| VAV Control | Single max with 30% minimums, dual max with 20% mins, dual max with 10% mins (using 10% is a simplification and it should really be based on min ventilation which can vary depending on space type)
| Occupancy Control | Assume occupancy sensors are NOT used in baseline, but can be a toggle for addition in the retrofit case for occupied standby mode. This allows zone airflows to setback AND minOA airflow at AHU to be reduced too.
| Demand controlled ventilation | For future consideration. Simple to just enable in high density rooms, but the % of high density rooms is a fixed assumption that may not be accurate. Defining a secondary space type might be an option, but would not capture envelope impacts correctly.
| Outside air control | Many older systems will not have explicit OA airflow control, or dynamic reset of setpoint. Consider adding this as a future input for consideration. Will have a bigger energy impact in more extreme climates. Hard to quantify existing condition (e.g. what is the input if the current control is just fixed 20% min damper position)
Post-Processing
| Building area | Model a fixed geometry with results normalized and scaled to user input for building area
| Primary/secondary space | Allow user entry of multiple building space type, or system attributes, with evaluation based on post-processing of multiple sets of modeled data scaled proportionally. If this is just post-processing, should be add a tertiary definition too?
| Schedule | Guideline 36 introduces Zone Groups, which allows different areas of the building to have different operating schedules, e.g. a multi tenant building would generally have systems running to serve the tenant with longer operating hours. G36 would facilitate scheduling savings so we could account for this by allowing separate baseline and post-retrofit schedules, and defining it for each primary, secondary space type.
| Heating Source | Model HW plant explicitly. Use post-processing to allow estimation of electric resistance heat source in future
| Campus Central Plant | Use post-processing to allow application to campus situations where HHW and CHW are provided from campus plant and billed on a thermal energy basis
Other
Some measures could potentially reduce peak demand. Should that be an explicit output from model too? Demand charge structures are complicated to provide as an input, but at least we could account for reduction in peak demand.